## Rev
Version | Description | Date | Author
2.0 | 1. Complete service action, service parts and its P/N for all alarm code 2. Index exist operation instruction (OI) | 2019-05-31 | Bryan
2.01 | Revising | 2020-05-15 | Bryan
2.02 | N/A
2.03 | Add 00400B Modify 00D008 | 2021-01-28 | Bryan

## AlarmCode
Cat. | Loc. | Alarm code | Description | Severity | Core | Service Action | Service Parts | Delta P/N | OI / Reference | Shown on LCD | Transfer to Backend
|  | 004001 | System input voltage is higher than workable range | 1 | V | 1. Check system input phase voltage that sould be less than 305V. 2. Check AC input voltage sense wire between input terminal bus bar and relay control board is connection well. 3. If item 1 and 2 are no problem, replace service parts. | Relay control board | 3798100032-S | D022_DC_Wallbox_Check system input voltage and sense wire.pdf DS08_DC_Wallbox_Replace relay control board_v1.0.pdf | Y | Y
|  | 004002 | System input voltage (L1, L2 or L3) is lower than workable range | 2 | V | 1. Check system input phase voltage (L1, L2 or L3) that sould be higher than 185V. 2. Check AC input voltage sense wire between input terminal bus bar and relay control board. 3. If item 1 and 2 are no problem, replace service parts. | Relay control board | 3798100032-S | D022_DC_Wallbox_Check system input voltage and sense wire.pdf DS08_DC_Wallbox_Replace relay control board_v1.0.pdf | Y | Y
|  | 004005 | Temperature of air inlet or input contactor is higher than workable range | 1 |  | 1. Check ambient temperature. If it is lower than 50°C, check cleanliness of air filter on both side. If air filter is dirty, replace filters. 2. Power cycle DCWB. If it shows 004007, follow its service action; if it still shows 004005, continuous step 3. 3. Wait 10 minutes, then try again. | SMR Air Filter System Air Filter | 3799997100-S 3799997200-S | DS07_DC_Wallbox_Replace filter_v2.1.pdf | Y | Y
|  | 004006 | Temperature of CCS combo charging plug is higher than workable range | 1 | V | 1. Confirm the charging gun temperature. If it is really higher than 85°C, check cleanliness of CCS charging gun contacts. 2. If charging gun temperature is lower than 85°C, wait 30 minutes then retry. 3. If the alarm still appears in 3 minutes, the temperature sensor in the charging gun is shorted. Replace service part. | CCS charging plug | 3799992800-S (REMA 6M, UL) 3799992900-S (REMA 4M, UL) 3799993000-S (Phoenix 4M, IEC) 3798100708-S (Phoenix 7M, IEC) | D010_DC_Wallbox_Charging gun temperature sensor_v1.0.pdf DS09_DC_Wallbox_Replace CCS Gun_v1.1.pdf | Y | Y
|  | 004007 | Air filters need to be replaced | 2 | V | 1. Replace service parts [PS] DCWB still can work | SMR Air Filter System Air Filter | 3799997100-S 3799997200-S | DS07_DC_Wallbox_Replace filter_v2.1.pdf | Y | Y
|  | 004008 | System fan error | 2 | V | 1. Replace service parts | System Fan | 3620889311 | DS16_DC_Wallbox_Replace Fan.pdf | Y | Y
|  | 004009 | System Init Failed | 1 |  | 1. Reboot charger 2. If still failed, replace service parts | CHAdeMO CSU | 3799706200-S (US CCS) 3798100015-S (EU CCS+CHAdeMO) 3798100016-S (US CCS+CHAdeMO) 3798100017-S (EU CCS) 3798100018-S (JP) | DS04_DC_Wallbox_Replace CHAdeMO CSU_v1.0.pdf | Y | Y
|  | 00400A | Emergency button is pressed | 1 | V | 1. Release emergency button 2. Check the contact of emergency button, if it is opened, replace it. 3. If it is closed, replace CHAdeMO CSU | Emergency Button CHAdeMO CSU | Emergency Button: 3000045300 CHAdeMO CSU: 3799706200-S (US CCS) 3798100015-S (EU CCS+CHAdeMO) 3798100016-S (US CCS+CHAdeMO) 3798100017-S (EU CCS) 3798100018-S (JP) | D021_DC_Wallbox_Check emergency button.pdf | Y | Y
|  | 00400B | User authorization is failed by backend while PnC is enable | 3 |  | Check the parameter "OCPP NonAuthorizedTag:" whether it is matching the setting in backend | N/A |  |  | Authentication fail | Y
|  | 00400D | Temperature sensor of air inlet is broken | 1 |  | 1. Check temperature sensor is connected well, and follows OI to inspect the sensor. 2. If the sensor is no problem, replace CHAdeMO CSU. 3. If the sensor is broken, replace temperatre sensor. | CHAdeMO CSU Temperature Sensor | CHAdeMO CSU: 3799706200-S (US CCS) 3798100015-S (EU CCS+CHAdeMO) 3798100016-S (US CCS+CHAdeMO) 3798100017-S (EU CCS) 3798100018-S (JP) Temperature Sensor: 091103PJ16 | D018_DC_Wallbox_Check inlet air thermal sensor.pdf DS04_DC_Wallbox_Replace CHAdeMO CSU_v1.0.pdf DS14_DC_Wallbox_Replace Inlet Air Thermal Sensor.pdf | Y | Y
|  | 00400E | Temperature sensor of input contactor is broken | 1 |  | 1. Check temperature sensor is connected well, and follows OI to inspect the sensor. 2. If the sensor is no problem, replace CHAdeMO CSU. 3. If the sensor is broken, replace temperatre sensor. | CHAdeMO CSU Temperature Sensor | CHAdeMO CSU: 3799706200-S (US CCS) 3798100015-S (EU CCS+CHAdeMO) 3798100016-S (US CCS+CHAdeMO) 3798100017-S (EU CCS) 3798100018-S (JP) Temperature Sensor: 091103PJ16 | D027_DC_Wallbox_Check temperature sensor of input contactor_v1.0.pdf DS04_DC_Wallbox_Replace CHAdeMO CSU_v1.0.pdf | Y | Y
|  | 00400F | SPD trigger | 1 | V | 1. If the contact of SPD is closed, replace SPD. 2. If the contact of SPD is open, check the wiring. 3. If still in alarm after wiring check, replace CHAdeMO CSU | SPD BD CHAdeMO CSU | SPD: 3798100038-S (1P) 3798100039-S (3P Y) 3798100040-S (3P delta) 3798100041-S (EU Y-connection, DELTA design) 3798E000000010-S (EU Y-connection, Phoenix contact) 3798100042-S (EU delta-connection, DELTA design) 0924011871 (EU delta-connection, Phooenix contact) 3798100043-S (3P CHAdeMO) 3798100044-S (3P CHAdeMO delta-connnection) CHAdeMO CSU: 3799706200-S (US CCS) 3798100015-S (EU CCS+CHAdeMO) 3798100016-S (US CCS+CHAdeMO) 3798100017-S (EU CCS) 3798100018-S (JP) | DS17_DC_Wallbox_Check and Replace SPD.pdf DS04_DC_Wallbox_Replace CHAdeMO CSU_v1.0.pdf | Y | Y
|  | 004010 | Output fuse on CCS relay board is broken | 1 | V | 1. Check the connectors CNB12 and CNB10 on relay control board are connected well 2. Replace service part. | Output Fuse | 0891170224 | DS18_DC_Wallbox_Replace output fuse.pdf | Y | Y
|  | 004011 | Output fuse on CHAdeMO relay board is broken | 1 | V | 1. Check the connectors CNB12 and CNB10 on relay control board are connected well. 2. Replace service part. | Output Fuse | 0891170224 | DS18_DC_Wallbox_Replace output fuse.pdf | Y | Y
|  | 004012 | Temperature sensor of CCS combo charging plug is broken | 1 | V | 1. Check the resistance of the CCS plug follow by OI. 2. If the temperature sensor is damaged, replace CCS charging plug. 3. If the temperature sensor is no problem, replace CHAdeMO CSU | CCS charging plug CHAdeMO CSU | CCS charging plug: 3799992800-S (REMA 6M, UL) 3799992900-S (REMA 4M, UL) 3799993000-S (Phoenix 4M, IEC) 3798100708-S (Phoenix 7M, IEC) CHAdeMO CSU: 3799706200-S (US CCS) 3798100015-S (EU CCS+CHAdeMO) 3798100016-S (US CCS+CHAdeMO) 3798100017-S (EU CCS) 3798100018-S (JP) | D010_DC_Wallbox_Charging gun temperature sensor_v1.0.pdf DS09_DC_Wallbox_Replace CCS Gun_v1.1.pdf DS04_DC_Wallbox_Replace CHAdeMO CSU_v1.0.pdf | Y | Y
|  | 004013 | Temperature of air inlet is lower than workable range | 2 |  | 1. Confirm ambient temperature. If it is lower than -40°C, there is no problem. 2. If ambient temperature is higher than -40°C, check temperature sensor is CLOSE circuit. 3. If temperature sensor is OPEN, replace service part. | Temperature Sensor | 091103PJ16 | D018_DC_Wallbox_Check inlet air thermal sensor.pdf DS14_DC_Wallbox_Replace Inlet Air Thermal Sensor.pdf | Y | Y
|  | 004014 | Stop charging by RFID | 3 |  | N/A |  |  |  | No | No
|  | 004015 | The plug-in times of CCS charging plug is more than 10000 times | 3 | V | 1. Consider to replace CCS charging plug 2. No matter replace charging gun or not, must update config file to reset this alarm | N/A |  | DA05_DC_Wallbox_Configuration update to setup parameter.pdf | No | Y
|  | 004016 | The plug-in times of CHAdeMO charging plug is more than 10000 times | 3 | V | 1. Consider to replace CHAdeMO charging plug 2. No matter replace charging gun or not, must update config file to reset this alarm | N/A |  | DA05_DC_Wallbox_Configuration update to setup parameter.pdf | No | Y
|  | 004017 | System is timeout if user doesn't plug-in in 5 minutes after authorized => Action item shall add check gun | 3 |  | 1. Plug in charging gun in 5 minutes after authorized. 2. To confirm the timeout value set in the backend system 3. If it is still fail and is using CHAdeMO plug, have to check CHAdeMO plug | N/A |  | D023_DC_Wallbox_Check CHAdeMO charging plug_v1.0.pdf | Y | Y
|  | 004018 | Charging time is up | 3 |  | 1. Check charger time out 2. Update time out by configuration tool | N/A |  | DA05_DC_Wallbox_Configuration update to setup parameter.pdf | Y | Y
|  | 004022 | Input voltage is drop (L1) | 1 | V | 1. Check AC input (especially for L1), and then restart if there is no problem. 2. Recommand to update the relay control board FW to v.01.03.01.01 or higher version 3. If still has same problem, replace Relay control board. 4. If still have same problem, replace CHAdeMO CSU. | Relay control board CHAdeMO CSU | Relay control board: 3798100032-S CHAdeMO CSU: 3799706200-S (US CCS) 3798100015-S (EU CCS+CHAdeMO) 3798100016-S (US CCS+CHAdeMO) 3798100017-S (EU CCS) 3798100018-S (JP) | D022_DC_Wallbox_Check system input voltage and sense wire.pdf DS08_DC_Wallbox_Replace relay control board_v1.0.pdf DS04_DC_Wallbox_Replace CHAdeMO CSU_v1.0.pdf | No | Y
|  | 004023 | System input voltage (L1) is lower than workable range | 1
|  | 004024 | System reach stop SoC | 3 |  | 1. It is normal behavior. Check the EV SoC 2. Rest the value of STOP SoC by updating config file. PS. This alarm is only saved in Log file and is not shown on LCM. This alarm is only related the setting of DCWB. | N/A |  | DA05_DC_Wallbox_Configuration update to setup parameter.pdf | No | No
|  | 004025 | System reach stop energy | 3 |  | 1. It is normal behavior. The alarm will be shown on LCM. 2. To reset the value of STOP ENERGY by updating config file. | N/A |  | DA05_DC_Wallbox_Configuration update to setup parameter.pdf | Y | No
|  | 005006 | Communication with SMR is broken | 1 |  | 1. Check AC input contactor can opearated at starting charge process. If the contactor fail, replace AC contactor. 2. Re-install SMR and check again. If it is failed, replace SMR. | AC contactor AC/DC rectifier (SMR) | AC contactor: 0729055551 SMR: DCM-123A A-S | D025_DC_Wallbox_AC contactor.pdf D024_DC_Wallbox_Check SMR.pdf DS13_DC_Wallbox_Replace AC contactor.pdf DS06_DC_Wallbox_Replace SMR.pdf | Y | Y
|  | 005007 | Communication with CCS controller is broken | 1 |  | 1. Unplug and re-plug CCS CSU and CHAdeMO CSU, then re-boot system. 2. If the alarm code still occur, ONLY replace CHAdeMO CSU. 3. If the alarm code still occur, ONLY replace CCS CSU. | CHAdeMO CSU CCS CSU | CHAdeMO CSU: 3799706200-S (US CCS) 3798100015-S (EU CCS+CHAdeMO) 3798100016-S (US CCS+CHAdeMO) 3798100017-S (EU CCS) 3798100018-S (JP) CCS CSU: 3799706300-S (US) 3798100019-S (EU) | DS04_DC_Wallbox_Replace CHAdeMO CSU_v1.0.pdf DS03_DC_Wallbox_Replace CCS CSU_v1.0.pdf | Y | Y
|  | 005008 | Communication with auxiliary power module is broken | 1 |  | 1. Check the RS485 cables (CNB8, CNB4) on relay control board is connected well. 2. Unplug and replug aux. power module, and then reboot system. 3. If the alarm code still occur, ONLY replace Aux. power module 4. If the alarm code still occur, ONLY replace replay control board | Auxiliary power module Relay control board | Aux. power module: DCM-121A A-S Relay control board: 3798100032-S | D026_DC_Wallbox_Check relay control board.pdf DS05_DC_Wallbox_Replace Aux power_v1.0.pdf DS08_DC_Wallbox_Replace relay control board_v1.0.pdf | Y | Y
|  | 005009 | Communication with relay control module is broken | 1 | V | 1. Check the RS485 cable (CNB8, CNB4) on relay control board is connected well. 2. If the alarm code still appear, ONLY replace replay control board | Relay control board | 3798100032-S | DS08_DC_Wallbox_Replace relay control board_v1.0.pdf | Y | Y
|  | 00500D | Communication with RFID module is broken | 1 |  | 1. Check the each cables on RFID module are connection well, and reboot system 2. If the alarm code still appear, replace service part | RFID module+reader | 3798C000000030-S | DS17_DC_Wallbox_Replace RFID module | Y | Y
|  | 00500E | 3G module is not ready | 2 | V | 1. Check the each calbes on 3G module are connection well. 2. Check LEDs on the 3G module if it is light on. If not light on, replace part (問EE LED燈號所代表的意思) | Communication BD | 3798100045-S (Huawei 609) 5505605078 (Huawei 709) 3798100046-S (Ublox) | DS12_DC_Wallbox_Replace 3G modem_v1.0.pdf | Y | Y
|  | 006002 | 3G connection is disconnected from internet | 2 | V | 1. Confirm/update the configuration setting 2. Confrim the 3G SIM card is available for using (ex: no problem in payment, internet) 3. Confirm the antenna cable is connected well on 3G module 4. Replace 3G module | Communication BD | 3798100045-S (Huawei 609) 5505605078 (Huawei 709) 3798100046-S (Ublox) | DS12_DC_Wallbox_Replace 3G modem_v1.0.pdf | No | Y
|  | 006003 | 3G connection is disconnected from backend office | 2 | V | 1. Confirm the OCPP related setting is correct in configuration 2. Confirm the 3G signal quality 3. Confirm the condition of backend system | N/A |  |  | No | No
|  | 006009 | Ethernet connection is disconnected from backend office | 2 | V | 1. Confrim the LAN cable is connected well on DCWB 2. Confirm the LAN network is no problem 3. Confirm the OCPP related setting is correct in configuration 4. Confirm the condition of backend system | N/A |  |  | Y | No
|  | 007001 | Power rectifier is abnormal | 3 |  | 1. Check LED on the SMR panel, if the LED color is RED, replace SMR. 2. If the LED color is GREEN, reboot system and check again. | AC/DC rectifier (SMR) | DCM-123A A-S | DS06_DC_Wallbox_Replace SMR_v1.1.pdf | Y | Y
|  | 007002 | Input voltage of power rectifier is higher than workable range | 3 |  | 1. Use multimeter to measure system input phase voltage, it should be less than 295V. (triger condition: 305V) 2. Replace service part | AC/DC rectifier (SMR) | DCM-123A A-S | D022_DC_Wallbox_Check system input voltage and sense wire.pdf DS06_DC_Wallbox_Replace SMR_v1.1.pdf | Y | Y
|  | 007003 | Input voltage of power rectifier is lower than workable range | 3 |  | 1. Use multimeter to measure system input phase voltage, it should be higher than 90V. (triger condition: 80V) 2. Replace service part | AC/DC rectifier (SMR) | DCM-123A A-S | D022_DC_Wallbox_Check system input voltage and sense wire.pdf DS06_DC_Wallbox_Replace SMR_v1.1.pdf | Y | Y
|  | 007004 | Output voltage is higher than workable range of power rectifier | 3 |  | 1. Check LED on the SMR panel, if the LED color is RED, replace SMR. 2. If the LED color is GREEN, reboot system and check again. | AC/DC rectifier (SMR) | DCM-123A A-S | DS06_DC_Wallbox_Replace SMR_v1.1.pdf | No | Y
|  | 007006 | The temperature of air inlet in power rectifier is higher than workable range | 3 |  | 1. If ambient temperature is higher than 55°C, power out wil be derating; if ambient temperature is higher than 75°C, charging will be shut-down. 2. Replace service part | AC/DC rectifier (SMR) | DCM-123A A-S | DS06_DC_Wallbox_Replace SMR_v1.1.pdf | No | Y
|  | 00700C | The fan inside power rectifier is broken | 3 |  | 1. Check LED on the SMR panel, if the LED color is RED, replace SMR. 2. If the LED color is GREEN, reboot system and check again. | AC/DC rectifier (SMR) | DCM-123A A-S | DS06_DC_Wallbox_Replace SMR_v1.1.pdf | No | Y
|  | 008003 | 5 volt for system controller is higher than workable range | 1 |  | 1. Replace service part. | Aux power | DCM-121A A-S | DS05_DC_Wallbox_Replace Aux power_v1.0.pdf | Y | Y
|  | 008004 | 5 volt for other system modules is higher than workable range | 1 |  | 1. Replace service part. | Aux power | DCM-121A A-S | DS05_DC_Wallbox_Replace Aux power_v1.0.pdf | Y | Y
|  | 008005 | 5 volt for CAN bus is higher than workable range | 1 |  | 1. Replace service part. | Aux power | DCM-121A A-S | DS05_DC_Wallbox_Replace Aux power_v1.0.pdf | Y | Y
|  | 008006 | 12 volt for other system modules is higher than workable range | 1 |  | 1. Replace service part. | Aux power | DCM-121A A-S | DS05_DC_Wallbox_Replace Aux power_v1.0.pdf | Y | Y
|  | 008007 | 12 volt for EV communication is higher than workable range | 1 |  | 1. Replace service part. | Aux power | DCM-121A A-S | DS05_DC_Wallbox_Replace Aux power_v1.0.pdf | Y | Y
|  | 008008 | 24 volt for relay control is higher than workable range | 1 |  | 1. Replace service part. | Aux power | DCM-121A A-S | DS05_DC_Wallbox_Replace Aux power_v1.0.pdf | Y | Y
|  | 008009 | 5 volt for system controller is lower than workable range | 1 |  | 1. Replace service part. | Aux power | DCM-121A A-S | DS05_DC_Wallbox_Replace Aux power_v1.0.pdf | Y | Y
|  | 00800A | 5 volt for other system modules is lower than workable range | 1 |  | 1. Replace service part. | Aux power | DCM-121A A-S | DS05_DC_Wallbox_Replace Aux power_v1.0.pdf | Y | Y
|  | 00800B | 5 volt for CAN bus is lower than workable range | 1 |  | 1. Replace service part. | Aux power | DCM-121A A-S | DS05_DC_Wallbox_Replace Aux power_v1.0.pdf | Y | Y
|  | 00800C | 12 volt for other system modules is lower than workable range | 1 |  | 1. Replace service part. | Aux power | DCM-121A A-S | DS05_DC_Wallbox_Replace Aux power_v1.0.pdf | Y | Y
|  | 00800D | 12 volt for EV communication is lower than workable range | 1 |  | 1. Replace service part. | Aux power | DCM-121A A-S | DS05_DC_Wallbox_Replace Aux power_v1.0.pdf | Y | Y
|  | 00800E | 24 volt for relay control is lower than workable range | 1 |  | 1. Replace service part. | Aux power | DCM-121A A-S | DS05_DC_Wallbox_Replace Aux power_v1.0.pdf | Y | Y
|  | 008019 | The ambinet temperature of auxiliary power is higher than workable range | 1 |  | 1. Check the ambient temperature if it is higher than 95°C. 2. Replace service part | Aux power | DCM-121A A-S | DS05_DC_Wallbox_Replace Aux power_v1.0.pdf | Y | Y
|  | 009001 | GFD trigger | 1 | V | 1. Use another EV to do charging, to see if the error accure as well. 2. Check charging plug. If it is broken, replace charging plug. 3. If charging plug is no problem, replace relay control board. | CCS or CHAdeMO Charging plug Relay control board | CCS charging plug: 3799992800-S (REMA 6M, UL) 3799992900-S (REMA 4M, UL) 3799993000-S (Phoenix 4M, IEC) 3798100708-S (Phoenix 7M, IEC) CHAdeMO charging plug: 3799993100-S (4M, UL) 3799993200-S (4M, IEC) 3799993300-S (4M, JP) Relay control board: 3798100032-S | D015_DC_Wallbox_Check CCS1 charging plug.pdf D016_DC_Wallbox_Check CCS2 charging plug.pdf D023_DC_Wallbox_Check CHAdeMO charging plug.pdf DS09_DC_Wallbox_Replace CCS Gun DS10_DC_Wallbox_Replace CHAdeMO Gun DS08_DC_Wallbox_Replace relay control board_v1.0.pdf | Y | Y
|  | 009003 | GFD pre-warnning | 3 | V | 1. Use another EV to do charging, to see if the error accure as well. 2. Check charging plug. If it is broken, replace charging plug. 3. If charging plug is no problem, replace relay control board. | CCS or CHAdeMO Charging plug Relay control board | CCS charging plug: 3799992800-S (REMA 6M, UL) 3799992900-S (REMA 4M, UL) 3799993000-S (Phoenix 4M, IEC) 3798100708-S (Phoenix 7M, IEC) CHAdeMO charging plug: 3799993100-S (4M, UL) 3799993200-S (4M, IEC) 3799993300-S (4M, JP) Relay control board: 3798100032-S | D015_DC_Wallbox_Check CCS1 charging plug.pdf D016_DC_Wallbox_Check CCS2 charging plug.pdf D023_DC_Wallbox_Check CHAdeMO charging plug.pdf DS09_DC_Wallbox_Replace CCS Gun DS10_DC_Wallbox_Replace CHAdeMO Gun DS08_DC_Wallbox_Replace relay control board_v1.0.pdf | No | Y
|  | 00A001 | Input contactor 1 is welding | 1 |  | 1. Under the power off, measure the AC contactor PIN-to-PIN, the result should be OPEN. If not, replace AC contactor. 2. If there is no problem of AC contactor measurement, replace Relay control board. | AC contactor Relay control board | AC contactor: 0729055551 Relay control board: 3798100032-S | D025_DC_Wallbox_Check AC contactor.pdf DS13_DC_Wallbox_Replace AC contactor_v1.0.pdf DS08_DC_Wallbox_Replace relay control board_v1.0.pdf | Y | Y
|  | 00A003 | Input contactor 2 is welding | 1 |  | 1. Under the power off, measure the AC contactor PIN-to-PIN, the result should be OPEN. If not, replace AC contactor. 2. If there is no problem of AC contactor measurement, replace Relay control board. | AC contactor Relay control board | AC contactor: 0729055551 Relay control board: 3798100032-S | D025_DC_Wallbox_Check AC contactor.pdf DS13_DC_Wallbox_Replace AC contactor_v1.0.pdf DS08_DC_Wallbox_Replace relay control board_v1.0.pdf | Y | Y
|  | 00A00E | The output relay for CCS charging is drived fault | 1 |  | 1. To check the wire from CCS relay board is connected well on Relay control board 2. Replace CCS relay board 3. Replace Relay cotrol board | CCS relay board Relay control board | CCS replay board: 3798100034-S (US) 3798100036-S (EU) Relay control board: 3798100032-S | DS01_DC_Wallbox_Replace CCS relay board_v1.0.pdf DS08_DC_Wallbox_Replace relay control board_v1.0.pdf | Y | Y
|  | 00A00F | The output relay for CHAdeMO charging is welding | 1 |  | 1. Remove CHAdeMO relay board and check the output fuse if it is OPEN. If not, replace CHAdeMO relay board. 2. If there is no problem for the output fuse, replace Relay control board | CHAdeMO relay board Relay control board | CHAdeMO replay board: 3798100035-S (US) 3798100037-S (EU) Relay control board: 3798100032-S | D017_DC_Wallbox_Check CCS Relay BD_v1.0.pdf DS02_DC_Wallbox_Replace CHAdeMO relay board_v1.0.pdf DS08_DC_Wallbox_Replace relay control board_v1.0.pdf | Y | Y
|  | 00A010 | The output relay for CHAdeMO charging is drived fault | 1 |  | 1. To check the wire from CHAdeMO Relay BD is connected well on Relay control board 2. Replace CHAdeMO Relay Board 3. Replace Relay Cotrol Board | CHAdeMO relay board Relay control board | CHAdeMO replay board: 3798100035-S (US) 3798100037-S (EU) Relay control board: 3798100032-S | DS02_DC_Wallbox_Replace CHAdeMO relay board_v1.0.pdf DS08_DC_Wallbox_Replace relay control board_v1.0.pdf | Y | Y
|  | 00A012 | The output pre-charge relay for CCS charging is drived fault | 1 |  | 1. To check the wire from CCS relay board is connected well on Relay control board 2. Replace CCS relay board 3. Replace Relay cotrol board | CCS relay board Relay control board | CCS replay board: 3798100034-S (US) 3798100036-S (EU) Relay control board: 3798100032-S | DS01_DC_Wallbox_Replace CCS relay board_v1.0.pdf DS08_DC_Wallbox_Replace relay control board_v1.0.pdf | Y | Y
|  | 00A013 | CCS pilot line is broken | 1 | V | 1. Power cycle DCWB, and then re-plug in to try again. 2. Inspection CCS charging plug, and replace it if the test is failed 3. Replace CCS CSU (CA board) | CCS charging plug CCS CSU | CCS charging plug: 3799992800-S (REMA 6M, UL) 3799992900-S (REMA 4M, UL) 3799993000-S (Phoenix 4M, IEC) 3798100708-S (Phoenix 7M, IEC) CCS CSU: 3799706300-S (US) 3798100019-S (EU) | D015_DC_Wallbox_Check CCS1 charging plug.pdf D016_DC_Wallbox_Check CCS2 charging plug.pdf DS09_DC_Wallbox_Replace CCS Gun DS03_DC_Wallbox_Replace CCS CSU_v1.0.pdf
|  | 00A014 | CCS proximity is broken (temporarily disabled) | 1 | V | 1. Power cycle DCWB, and then re-plug in to try again. 2. Inspection CCS charging plug, and replace it if the test is failed 3. Replace CCS CSU (CA board) | CCS charging plug CCS CSU | CCS charging plug: 3799992800-S (REMA 6M, UL) 3799992900-S (REMA 4M, UL) 3799993000-S (Phoenix 4M, IEC) 3798100708-S (Phoenix 7M, IEC) CCS CSU: 3799706300-S (US) 3798100019-S (EU) | D015_DC_Wallbox_Check CCS1 charging plug.pdf D016_DC_Wallbox_Check CCS2 charging plug.pdf DS09_DC_Wallbox_Replace CCS Gun DS03_DC_Wallbox_Replace CCS CSU_v1.0.pdf
|  | 00B001 | The firmware update of auxiliary power module is failure | 1 |  | LCM shows "update failed", not alarm code. 1. Try again | N/A |  |  | No | Y
|  | 00B002 | The firmware update of relay control module is failure | 1 | V | 1. Must be BA FW v2.01 or higher version 2. Try again 3. If still fail, provide the updated files and downloaded log file to BU service for analysis | N/A |  |  | No | Y
|  | 00B003 | The firmware update of LCM module is failure | 1 |  | 1. Try again 2. If still fail, provide the updated files and downloaded log file to BU service for analysis | N/A |  |  | No | Y
|  | 00B004 | The firmware update of CCS charging module is failure | 1 |  | 1. When updgrade CA FW v1.06(or lower ver.) to v1.08(or higher ver.), must happened "CCS CSU failed" on LCM. To confirm the actual results via log. 2. Try again. 3. If still fail, provide the updated files and downloaded log file to BU service for analysis | N/A |  |  | No | Y
|  | 00B005 | The firmware update of CHAdeMO charging module is failure | 1 |  | 1. Try again 2. If still fail, provide the updated files and downloaded log file to BU service for analysis | N/A |  |  | No | Y
|  | 00B006 | The firmware update of power converter module is failure | 1 |  | 1. Try again 2. If still fail, provide the updated files and downloaded log file to BU service for analysis | N/A |  |  | No | Y
|  | 00C002 | CCS1 proximity is disconnected | 1 | V | 1. Replug the charging gun for test again, to see if the error 00A014 occurs. If yes, follow the service action of 00A014. 2. If it still occurs 00C002, replace CCS CSU (CA board) | CCS CSU | 3799706300-S (US) 3798100019-S (EU) | DS03_DC_Wallbox_Replace CCS CSU_v1.0.pdf | Y | Y
|  | 00C100 | SLAC - No data | 1 | V | 1. Use another EV to do test. If occur same error, replace CCS CSU. 2. Replace CCS charging plug 3. Download log file and WireShark file, and contact BU service for further action. | CCS CSU CCS charging plug | CCS CSU: 3799706300-S (US) 3798100019-S (EU) CCS charging plug: 3799992800-S (REMA 6M, UL) 3799992900-S (REMA 4M, UL) 3799993000-S (Phoenix 4M, IEC) 3798100708-S (Phoenix 7M, IEC) | DS03_DC_Wallbox_Replace CCS CSU_v1.0.pdf DS09_DC_Wallbox_Replace CCS Gun DA01_DC_Wallbox_Download log file by USB_v1.0.pdf D012_DC_Wallbox_Download communication package by WireShark_v1.0.pdf | Y | Y
|  | 00C101 | SLAC error | 1 | V | 1. Use another EV to do test. To tell the problem is related to EV or charger. 2. Download log file and WireShark file, and contact BU service for further action. | N/A |  | DA01_DC_Wallbox_Download log file by USB_v1.0.pdf D012_DC_Wallbox_Download communication package by WireShark_v1.0.pdf | Y | Y
|  | 00C102 | SDP error | 1 | V | 1. Use another EV to do test. To tell the problem is related to EV or charger. 2. Download log file and WireShark file, and contact BU service for further action. | N/A |  | DA01_DC_Wallbox_Download log file by USB_v1.0.pdf D012_DC_Wallbox_Download communication package by WireShark_v1.0.pdf | Y | Y
|  | 00C103 | TCP error | 1 | V | 1. Use another EV to do test. To tell the problem is related to EV or charger. 2. Download log file and WireShark file, and contact BU service for further action. | N/A |  | DA01_DC_Wallbox_Download log file by USB_v1.0.pdf D012_DC_Wallbox_Download communication package by WireShark_v1.0.pdf | Y | Y
|  | 00C104 | V2G error - Idle | 1 | V | 1. Use another EV to do test. To tell the problem is related to EV or charger. 2. Download log file and WireShark file, and contact BU service for further action. | N/A |  | DA01_DC_Wallbox_Download log file by USB_v1.0.pdf D012_DC_Wallbox_Download communication package by WireShark_v1.0.pdf | Y | Y
|  | 00C105 | V2G error - supportedAppProtocol | 1 | V | 1. Use another EV to do test. To tell the problem is related to EV or charger. 2. Download log file and WireShark file, and contact BU service for further action. | N/A |  | DA01_DC_Wallbox_Download log file by USB_v1.0.pdf D012_DC_Wallbox_Download communication package by WireShark_v1.0.pdf | Y | Y
|  | 00C106 | V2G error - SessionSetup | 1 | V | 1. Use another EV to do test. To tell the problem is related to EV or charger. 2. Download log file and WireShark file, and contact BU service for further action. | N/A |  | DA01_DC_Wallbox_Download log file by USB_v1.0.pdf D012_DC_Wallbox_Download communication package by WireShark_v1.0.pdf | Y | Y
|  | 00C107 | V2G error - ServiceDiscovery | 1 | V | 1. Use another EV to do test. To tell the problem is related to EV or charger. 2. Download log file and WireShark file, and contact BU service for further action. | N/A |  | DA01_DC_Wallbox_Download log file by USB_v1.0.pdf D012_DC_Wallbox_Download communication package by WireShark_v1.0.pdf | Y | Y
|  | 00C108 | V2G error - ServicePaymentSelection | 1 | V | 1. Use another EV to do test. To tell the problem is related to EV or charger. 2. Download log file and WireShark file, and contact BU service for further action. | N/A |  | DA01_DC_Wallbox_Download log file by USB_v1.0.pdf D012_DC_Wallbox_Download communication package by WireShark_v1.0.pdf | Y | Y
|  | 00C109 | V2G error - ContractAuthentication | 1 | V | 1. Use another EV to do test. To tell the problem is related to EV or charger. 2. Download log file and WireShark file, and contact BU service for further action. | N/A |  | DA01_DC_Wallbox_Download log file by USB_v1.0.pdf D012_DC_Wallbox_Download communication package by WireShark_v1.0.pdf | Y | Y
|  | 00C10A | V2G error - ChargeParameterDiscovery | 1 | V | 1. Use another EV to do test. To tell the problem is related to EV or charger. 2. Download log file and WireShark file, and contact BU service for further action. | N/A |  | DA01_DC_Wallbox_Download log file by USB_v1.0.pdf D012_DC_Wallbox_Download communication package by WireShark_v1.0.pdf | Y | Y
|  | 00C10B | V2G error - CableCheck | 1 | V | 1. Use another EV to do test. To tell the problem is related to EV or charger. 2. Download log file and WireShark file, and contact BU service for further action. | N/A |  | DA01_DC_Wallbox_Download log file by USB_v1.0.pdf D012_DC_Wallbox_Download communication package by WireShark_v1.0.pdf | Y | Y
|  | 00C10C | V2G error - PreCharge | 1 | V | 1. Use another EV to do test. To tell the problem is related to EV or charger. 2. Download log file and WireShark file, and contact BU service for further action. | N/A |  | DA01_DC_Wallbox_Download log file by USB_v1.0.pdf D012_DC_Wallbox_Download communication package by WireShark_v1.0.pdf | Y | Y
|  | 00C10D | V2G error - PowerDelivery | 1 | V | 1. Use another EV to do test. To tell the problem is related to EV or charger. 2. Download log file and WireShark file, and contact BU service for further action. | N/A |  | DA01_DC_Wallbox_Download log file by USB_v1.0.pdf D012_DC_Wallbox_Download communication package by WireShark_v1.0.pdf | Y | Y
|  | 00C10E | V2G error - CurrentDemand | 1 | V | 1. Use another EV to do test. To tell the problem is related to EV or charger. 2. Download log file and WireShark file, and contact BU service for further action. | N/A |  | DA01_DC_Wallbox_Download log file by USB_v1.0.pdf D012_DC_Wallbox_Download communication package by WireShark_v1.0.pdf | Y | Y
|  | 00C202 | Timeout error - ReadyToCharge | 1 | V | 1. Use another EV to do test. To tell the problem is related to EV or charger. 2. Download log file and WireShark file, and contact BU service for further action. | N/A |  | DA01_DC_Wallbox_Download log file by USB_v1.0.pdf D012_DC_Wallbox_Download communication package by WireShark_v1.0.pdf | Y | Y
|  | 00C203 | CableCheck error - SMR Vout is less than Vcmd | 1 | V | 1. Use another EV to do test. To tell the problem is related to EV or charger. 2. Replace the 2 units of SMR on DCWB 3. Download log file and WireShark file, and contact BU service for further action. | AC/DC rectifier (SMR) | DCM-123A A-S | DS06_DC_Wallbox_Replace SMR_v1.1.pdf DA01_DC_Wallbox_Download log file by USB_v1.0.pdf D012_DC_Wallbox_Download communication package by WireShark_v1.0.pdf | Y | Y
|  | 00C204 | CableCheck error - SMR Vout is over 20V | 1 | V | 1. Use another EV to do test. To tell the problem is related to EV or charger. 2. Replace the SMR on DCWB one by one. 3. Download log file and WireShark file, and contact BU service for further action. | AC/DC rectifier (SMR) | DCM-123A A-S | DS06_DC_Wallbox_Replace SMR_v1.1.pdf DA01_DC_Wallbox_Download log file by USB_v1.0.pdf D012_DC_Wallbox_Download communication package by WireShark_v1.0.pdf | Y | Y
|  | 00C205 | CableCheck error - Output voltage is over 60V before insulation test | 1 | V | 1. Use another EV to do test. To tell the problem is related to EV or charger. 2. Replace the SMR on DCWB one by one. 3. Download log file and WireShark file, and contact BU service for further action. | AC/DC rectifier (SMR) | DCM-123A A-S | DS06_DC_Wallbox_Replace SMR_v1.1.pdf DA01_DC_Wallbox_Download log file by USB_v1.0.pdf D012_DC_Wallbox_Download communication package by WireShark_v1.0.pdf | Y | Y
|  | 00C206 | CableCheck error - Output current is over 2A in insulation test | 1 | V | 1. Check the CCS charging plug. If it is fail, replace charging plug. 2. Use another EV to do test. To tell the problem is related to EV or charger. 3. Replace CCS relay board or CHAdeMO relay board. | CCS charging plug CCS relay board CHAdeMO relay board | CCS charging plug: 3799992800-S (REMA 6M, UL) 3799992900-S (REMA 4M, UL) 3799993000-S (Phoenix 4M, IEC) 3798100708-S (Phoenix 7M, IEC) CCS replay board: 3798100034-S (US) 3798100036-S (EU) CHAdeMO relay board: 3798100035-S (US) 3798100037-S (EU) | D015_DC_Wallbox_Check CCS1 charging plug.pdf D016_DC_Wallbox_Check CCS2 charging plug.pdf DS09_DC_Wallbox_Replace CCS Gun DS01_DC_Wallbox_Replace CCS relay board_v1.0.pdf DS02_DC_Wallbox_Replace CHAdeMO relay board_v1.0.pdf | Y | Y
|  | 00C207 | Precharge error - Output voltage is less than EV Vcmd | 3 | V | 1. Replace CCS relay board 2. Use another EV to do test. To tell the problem is related to EV or charger. 3. Download log file and WireShark file, and contact BU service for further action. | CCS relay board | 3798100034-S (US) 3798100036-S (EU) | DS01_DC_Wallbox_Replace CCS relay board_v1.0.pdf DA01_DC_Wallbox_Download log file by USB_v1.0.pdf D012_DC_Wallbox_Download communication package by WireShark_v1.0.pdf | Y | Y
|  | 00C208 | Precharge error - Output current is over 1.5A in precharge | 3 | V | 1. Replace CCS relay board 2. Use another EV to do test. To tell the problem is related to EV or charger. 3. Download log file and WireShark file, and contact BU service for further action. | CCS relay board | 3798100034-S (US) 3798100036-S (EU) | DS01_DC_Wallbox_Replace CCS relay board_v1.0.pdf DA01_DC_Wallbox_Download log file by USB_v1.0.pdf D012_DC_Wallbox_Download communication package by WireShark_v1.0.pdf | Y | Y
|  | 00C300 | EV error - FAILED_RESSTemperatureInhibit | 1 | V | This error is caused by EV battery tempature abnormal. 1. Cool down or warm up EV battery to do charging again. 2. Use another EV to do charging test. To tell the problem is related to EV or charger. 3. Download log file and WireShark file, and contact BU service for further action. | N/A |  |  | Y | Y
|  | 00C301 | EV error - FAILED_EVShiftPosition | 1 | V | EV is not at Parking gear | N/A |  |  | Y | Y
|  | 00C302 | EV error - FAILED_ChargerConnectorLockFault | 1 | V | Cannot lock or unlock with EV. 1. Replace CCS charging plug 2. Problem is caused by EV | CCS charging plug | 3799992800-S (REMA 6M, UL) 3799992900-S (REMA 4M, UL) 3799993000-S (Phoenix 4M, IEC) 3798100708-S (Phoenix 7M, IEC | DS09_DC_Wallbox_Replace CCS Gun_v1.1.pdf | Y | Y
|  | 00C303 | EV error - FAILED_EVRESSMalfunction | 1 | V | Alarm is from EV battery management system. 1. Use another EV to do charging test. To tell the problem is related to EV or charger. 2. Download log file and WireShark file, and contact BU service for further action. | N/A |  |  | Y | Y
|  | 00C304 | EV error - FAILED_ChargingCurrentdifferential | 1 | V | The SMR output current is not achieved to EV need. 1. Replace SMR one-by-one 2. Download log file and WireShark file, and contact BU service for further action. | AC/DC rectifier (SMR) | DCM-123A A-S | DS06_DC_Wallbox_Replace SMR_v1.1.pdf DA01_DC_Wallbox_Download log file by USB_v1.0.pdf D012_DC_Wallbox_Download communication package by WireShark_v1.0.pdf | Y | Y
|  | 00C305 | EV error - FAILED_ChargingVoltageOutOfRange | 1 | V | The SMR output voltage is over EV operation range. 1. Replace SMR one-by-one 2. Download log file and WireShark file, and contact BU service for further action. | AC/DC rectifier (SMR) | DCM-123A A-S | DS06_DC_Wallbox_Replace SMR_v1.1.pdf DA01_DC_Wallbox_Download log file by USB_v1.0.pdf D012_DC_Wallbox_Download communication package by WireShark_v1.0.pdf | Y | Y
|  | 00C306 | EV error - FAILED_Reserved_A | 1 | V | 1. Use another EV to do charging test. To tell the problem is related to EV or charger. 2. Download log file and WireShark file, and contact BU service for further action. | N/A |  |  | Y | Y
|  | 00C307 | EV error - FAILED_Reserved_B | 1 | V | 1. Use another EV to do charging test. To tell the problem is related to EV or charger. 2. Download log file and WireShark file, and contact BU service for further action. | N/A |  |  | Y | Y
|  | 00C308 | EV error - FAILED_Reserved_C | 1 | V | 1. Use another EV to do charging test. To tell the problem is related to EV or charger. 2. Download log file and WireShark file, and contact BU service for further action. | N/A |  |  | Y | Y
|  | 00C309 | EV error - FAILED_ChargingSystemIncompatibility | 1 | V | Download log file and WireShark file, and contact BU service for further action | N/A |  |  | Y | Y
|  | 00C30A | EV error - FAILED_NoData | 1 | V | Download log file and WireShark file, and contact BU service for further action | N/A |  |  | Y | Y
|  | 00C30B | Stop charging at supportedAppProtocol | 1 | V | Download log file and WireShark file, and contact BU service for further action | N/A |  |  | Y | Y
|  | 00C30C | Stop charging at SessionSetup | 1 | V | Duplicate the failure symptom and record the WireShark data at the same time. Then provide the log file and Wireshark file to BU service for further action. | N/A |  |  | Y | Y
|  | 00C30D | Stop charging at ServiceDiscovery | 1 | V | Duplicate the failure symptom and record the WireShark data at the same time. Then provide the log file and Wireshark file to BU service for further action. | N/A |  |  | Y | Y
|  | 00C30E | Stop charging at ServicePaymentSelection | 1 | V | Duplicate the failure symptom and record the WireShark data at the same time. Then provide the log file and Wireshark file to BU service for further action. | N/A |  |  | Y | Y
|  | 00C30F | Stop charging at ContractAuthentication | 1 | V | Duplicate the failure symptom and record the WireShark data at the same time. Then provide the log file and Wireshark file to BU service for further action. | N/A |  |  | Y | Y
|  | 00C310 | Stop charging at ChargeParameterDiscovery | 1 | V | Duplicate the failure symptom and record the WireShark data at the same time. Then provide the log file and Wireshark file to BU service for further action. | N/A |  |  | Y | Y
|  | 00C311 | Stop charging at CableCheck | 1 | V | Duplicate the failure symptom and record the WireShark data at the same time. Then provide the log file and Wireshark file to BU service for further action. | N/A |  |  | Y | Y
|  | 00C312 | Stop charging at PreCharge | 1 | V | Duplicate the failure symptom and record the WireShark data at the same time. Then provide the log file and Wireshark file to BU service for further action. | N/A |  |  | Y | Y
|  | 00C313 | Stop charging at CurrentDemand | 1 | V | Duplicate the failure symptom and record the WireShark data at the same time. Then provide the log file and Wireshark file to BU service for further action. | N/A |  |  | Y | Y
|  | 00C314 | Stop charging at CurrentDemand by PowerDelivery(BulkChargingComplete) | 3 | V | Duplicate the failure symptom and record the WireShark data at the same time. Then provide the log file and Wireshark file to BU service for further action. | N/A |  |  | Y | Y
|  | 00C315 | Stop charging at CurrentDemand by PowerDelivery(ChargingComplete) | 3 | V | Duplicate the failure symptom and record the WireShark data at the same time. Then provide the log file and Wireshark file to BU service for further action. | N/A |  |  | Y | Y
|  | 00C316 | Stop charging by pilot A | 1 | V | 1. Replace CCS CSU 2. Duplicate the failure symptom and record the WireShark data at the same time. Then provide the log file and Wireshark file to BU service for further action. | CCS CSU | 3799706300-S (US) 3798100019-S (EU) | DS03_DC_Wallbox_Replace CCS CSU_v1.0.pdf | Y | Y
|  | 00C317 | Stop charging by pilot B | 1 | V | 1. Replace CCS CSU 2. Duplicate the failure symptom and record the WireShark data at the same time. Then provide the log file and Wireshark file to BU service for further action. 3. 充飽電是否有可能觸發，待查 | CCS CSU | 3799706300-S (US) 3798100019-S (EU) | DS03_DC_Wallbox_Replace CCS CSU_v1.0.pdf | Y | Y
|  | 00C318 | Stop charging by pilot E, F or error | 1 | V | 1. Replace CCS CSU 2. Duplicate the failure symptom and record the WireShark data at the same time. Then provide the log file and Wireshark file to BU service for further action. | CCS CSU | 3799706300-S (US) 3798100019-S (EU) | DS03_DC_Wallbox_Replace CCS CSU_v1.0.pdf | Y | Y
|  | 00D001 | No charging permission come from CHAdeMO EV | 3 | V | 1. Check the CHAdeMO charging plug, and to replace it if the test result is fail. 2. Use another EV to do charging test. To tell the problem is related to EV or charger 3. Duplicate the failure symptom and record the CAN data via PCAN at the same time. (if available) 4. Provide the log file and PCAN file to BU service for further action. | CHAdeMO charging plug | 3799993100-S (4M, UL) 3799993200-S (4M, IEC) 3799993300-S (4M, JP) | D023_DC_Wallbox_Check CHAdeMO charging plug_v1.0.pdf DS10_DC_Wallbox_Replace CHAdeMO Gun_1.0.pdf D014_DC_Wallbox_Download communication package by PCAN_v2.0.pdf | Y | Y
|  | 00D003 | Target battery voltage is higher than available output voltage | 1 | V | Not an issue. The charging spec. is incompatible between EV and charger | N/A |  |  | Y | Y
|  | 00D004 | Battery undervoltage | 1 | V | The problem is caused by EV. Recommend to confirm the EV battery healthy | N/A |  |  | Y | Y
|  | 00D005 | Battery overvoltage | 1 | V | The problem is caused by EV. Recommend to confirm the EV battery healthy | N/A |  |  | Y | Y
|  | 00D006 | Present output current is different from target current | 1 | V | 1. Retry to see if it occurs another alarm error. 2. If it occurs 00D006 again, replace SMR one-by-one | AC/DC rectifier (SMR) | DCM-123A A-S | DS06_DC_Wallbox_Replace SMR_v1.1.pdf | Y | Y
|  | 00D007 | Battery OTP come from CHAdeMO EV | 1 | V | This error is caused by EV battery over tempature. 1. Wait 10 mint to cool down EV battery tempature and then do charging again. | N/A |  |  | Y | Y
|  | 00D008 | Present output voltage deviated from battery voltage measured by EV over a level defined by EV | 1 | V | 1. Re-boot machine, retry charging to see if there is any change. 2. If it occurs 00D008 again, re-install all wires or cables of relay control board. 3. If 00D008 still occurs, replace relay control board. | Relay control board | 3798100032-S | DS08_DC_Wallbox_Replace relay control board_v1.0.pdf | Y | Y
|  | 00D009 | Position shift alarm is come from CHAdeMO EV | 1 | V | EV is not at Parking gear | N/A |  |  | Y | Y
|  | 00D00A | EV other fault is come from CHAdeMO EV | 1 | V | 1. Use another EV to do charging test. To tell the problem is related to EV or charger 2. Duplicate the failure symptom and record the CAN data via PCAN at the same time. (if available) 3. Provide the log file and PCAN file to BU service for further action. | N/A |  | D014_DC_Wallbox_Download communication package by PCAN_v2.0.pdf | Y | Y
|  | 00D00B | CHAdeMO connector lock is broken | 1 | V | 1. Replug the charging plug and to make sure that the plug is completely inserted. 2. Replace CHAdeMO charging plug 3. Replace CHAdeMO CSU | CHAdeMO charging plug CHAdeMO CSU | CHAdeMO charging plug: 3799993100-S (4M, UL) 3799993200-S (4M, IEC) 3799993300-S (4M, JP) CHAdeMO CSU: 3799706200-S (US CCS) 3798100015-S (EU CCS+CHAdeMO) 3798100016-S (US CCS+CHAdeMO) 3798100017-S (EU CCS) 3798100018-S (JP) | DS10_DC_Wallbox_Replace CHAdeMO Gun DS04_DC_Wallbox_Replace CHAdeMO CSU_v1.0.pdf | Y | Y
|  | 00D00D | Battery malfunction - Target battery voltage is higher than maximum battery voltage | 1 | V | This problem is definitely from EV. | N/A |  |  | Y | Y
|  | 00D00E | Charging current request is higher than available output current | 1 | V | 1. Use another EV to do charging test. To tell the problem is related to EV or charger 2. Duplicate the failure symptom and record the CAN data via PCAN at the same time. (if available) 3. Provide the log file and PCAN file to BU service for further action. | N/A |  | D014_DC_Wallbox_Download communication package by PCAN_v2.0.pdf | Y | Y
|  | 00D00F | Timeout error - Start of Vehicle CAN data | 1 | V | 1. Check the CHAdeMO charging plug, and to replace it if the test result is fail. 2. Replace CHAdeMO CSU 3. Use another EV to do charging test. To tell the problem is related to EV or charger | CHAdeMO charging plug CHAdeMO CSU | CHAdeMO charging plug: 3799993100-S (4M, UL) 3799993200-S (4M, IEC) 3799993300-S (4M, JP) CHAdeMO CSU: 3799706200-S (US CCS) 3798100015-S (EU CCS+CHAdeMO) 3798100016-S (US CCS+CHAdeMO) 3798100017-S (EU CCS) 3798100018-S (JP) | D023_DC_Wallbox_Check CHAdeMO charging plug_v1.0.pdf DS10_DC_Wallbox_Replace CHAdeMO Gun DS04_DC_Wallbox_Replace CHAdeMO CSU_v1.0.pdf | Y | Y
|  | 00D010 | Timeout error - CAN communication fault | 1 | V | 1. Do charging again 2. Check the CHAdeMO charging plug, and to replace it if the test result is fail. 3. Replace CHAdeMO CSU 4. Duplicate the failure symptom and record the CAN data via PCAN at the same time. (if available) 5. Provide the log file and PCAN file to BU service for further action. | CHAdeMO charging plug CHAdeMO CSU | CHAdeMO charging plug: 3799993100-S (4M, UL) 3799993200-S (4M, IEC) 3799993300-S (4M, JP) CHAdeMO CSU: 3799706200-S (US CCS) 3798100015-S (EU CCS+CHAdeMO) 3798100016-S (US CCS+CHAdeMO) 3798100017-S (EU CCS) 3798100018-S (JP) | D023_DC_Wallbox_Check CHAdeMO charging plug_v1.0.pdf DS10_DC_Wallbox_Replace CHAdeMO Gun DS04_DC_Wallbox_Replace CHAdeMO CSU_v1.0.pdf | Y | Y
|  | 00D011 | Timeout error - Charging enable | 1 | V | 1. Do charging again 2. Check the CHAdeMO charging plug, and to replace it if the test result is fail. 3. Replace CHAdeMO CSU 4. Duplicate the failure symptom and record the CAN data via PCAN at the same time. (if available) 5. Provide the log file and PCAN file to BU service for further action. | CHAdeMO charging plug CHAdeMO CSU | CHAdeMO charging plug: 3799993100-S (4M, UL) 3799993200-S (4M, IEC) 3799993300-S (4M, JP) CHAdeMO CSU: 3799706200-S (US CCS) 3798100015-S (EU CCS+CHAdeMO) 3798100016-S (US CCS+CHAdeMO) 3798100017-S (EU CCS) 3798100018-S (JP) | D023_DC_Wallbox_Check CHAdeMO charging plug_v1.0.pdf DS10_DC_Wallbox_Replace CHAdeMO Gun DS04_DC_Wallbox_Replace CHAdeMO CSU_v1.0.pdf | Y | Y
|  | 00D012 | Timeout error - EV contactor close | 1 | V | 1. Do charging again. If same error occurs, use another EV to do test and accordingly tell is this issue related to EV or charger; if it occurs another alarm code, to follow related service action. 2. Duplicate the failure symptom and record the CAN data via PCAN at the same time. (if available) 3. Provide the log file and PCAN file to BU service for further action. | N/A |  | D014_DC_Wallbox_Download communication package by PCAN_v2.0.pdf | Y | Y
|  | 00D013 | Timeout error - Charging current request | 1 | V | 1. Do charging again. If same error occurs, use another EV to do test and accordingly tell is this issue related to EV or charger; if it occurs another alarm code, to follow related service action. 2. Duplicate the failure symptom and record the CAN data via PCAN at the same time. (if available) 3. Provide the log file and PCAN file to BU service for further action. | N/A |  | D014_DC_Wallbox_Download communication package by PCAN_v2.0.pdf | Y | Y
|  | 00D014 | Insulation error - SMR Vout is less than Vcmd | 1 | V | 1. Use another EV to do test. To tell the problem is related to EV or charger. 2. Replace the 2 units of SMR on DCWB 3. Download log file and record CAN data by PCAN, and contact BU service for further action. | AC/DC rectifier (SMR) | DCM-123A A-S | DS06_DC_Wallbox_Replace SMR_v1.1.pdf DA01_DC_Wallbox_Download log file by USB_v1.0.pdf D014_DC_Wallbox_Download communication package by PCAN_v2.0.pdf | Y | Y
|  | 00D015 | Insulation error - SMR Vout is over 20V | 1 | V | 1. Use another EV to do test. To tell the problem is related to EV or charger. 2. Replace the SMR on DCWB one by one. 3. Download log file and record CAN data by PCAN, and contact BU service for further action. | AC/DC rectifier (SMR) | DCM-123A A-S | DS06_DC_Wallbox_Replace SMR_v1.1.pdf DA01_DC_Wallbox_Download log file by USB_v1.0.pdf D014_DC_Wallbox_Download communication package by PCAN_v2.0.pdf | Y | Y
|  | 00D016 | Insulation error - Output voltage over 10V before insulation test | 1 | V | 1. Use another EV to do test. To tell the problem is related to EV or charger. 2. Replace the SMR on DCWB one by one. 3. Download log file and record CAN data by PCAN, and contact BU service for further action. | AC/DC rectifier (SMR) | DCM-123A A-S | DS06_DC_Wallbox_Replace SMR_v1.1.pdf DA01_DC_Wallbox_Download log file by USB_v1.0.pdf D014_DC_Wallbox_Download communication package by PCAN_v2.0.pdf | Y | Y
|  | 00D017 | Insulation error - Output voltage over 20V after insulation test | 1 | V | 1. Use another EV to do test. To tell the problem is related to EV or charger. 2. Replace the SMR on DCWB one by one. 3. Download log file and record CAN data by PCAN, and contact BU service for further action. | AC/DC rectifier (SMR) | DCM-123A A-S | DS06_DC_Wallbox_Replace SMR_v1.1.pdf DA01_DC_Wallbox_Download log file by USB_v1.0.pdf D014_DC_Wallbox_Download communication package by PCAN_v2.0.pdf | Y | Y
|  | 00D018 | Insulation error - Output current is over 2A in insulation test | 1 | V | 1. Check the CHAdeMO charging plug. If it is fail, replace charging plug. 2. Use another EV to do test. To tell the problem is related to EV or charger. 3. Replace CCS relay board or CHAdeMO relay board. | CHAdeMO charging plug CCS relay board CHAdeMO relay board | CHAdeMO charging plug: 3799993100-S (4M, UL) 3799993200-S (4M, IEC) 3799993300-S (4M, JP) CCS replay board: 3798100034-S (US) 3798100036-S (EU) CHAdeMO relay board: 3798100035-S (US) 3798100037-S (EU) | D023_DC_Wallbox_Check CHAdeMO charging plug_v1.0.pdf DS10_DC_Wallbox_Replace CHAdeMO Gun DS01_DC_Wallbox_Replace CCS relay board_v1.0.pdf DS02_DC_Wallbox_Replace CHAdeMO relay board_v1.0.pdf | Y | Y
|  | 00D019 | Vehicle voltage error - Output voltage over 10V after charging | 1 | V | 1. Use another EV to do test. To tell the problem is related to EV or charger. 2. Replace the SMR on DCWB one by one. 3. Download log file and record CAN data by PCAN, and contact BU service for further action. | AC/DC rectifier (SMR) | DCM-123A A-S | DS06_DC_Wallbox_Replace SMR_v1.1.pdf DA01_DC_Wallbox_Download log file by USB_v1.0.pdf D014_DC_Wallbox_Download communication package by PCAN_v2.0.pdf | Y | Y
|  | 00D01B | CHAdeMO system error - process | 1 |  | 1. Replace parts | CHAdeMO CSU | 3799706200-S (US CCS) 3798100015-S (EU CCS+CHAdeMO) 3798100016-S (US CCS+CHAdeMO) 3798100017-S (EU CCS) 3798100018-S (JP) | DS04_DC_Wallbox_Replace CHAdeMO CSU_v1.0.pdf | No | Y
|  | 00D01C | CHAdeMO EV permission disable time out after charging | 1 | V | 1. Do charging again or use another EV to do charging test. To tell the problem is related to EV or charger 2. Duplicate the failure symptom and record the CAN data via PCAN at the same time. (if available) 3. Provide the log file and PCAN file to BU service for further action. | N/A |  |  | Y | Y
|  | 00D01D | CHAdeMO EV contactor open time out after charging | 1 | V | 1. Do charging again or use another EV to do charging test. To tell the problem is related to EV or charger 2. Duplicate the failure symptom and record the CAN data via PCAN at the same time. (if available) 3. Provide the log file and PCAN file to BU service for further action. | N/A |  |  | Y | Y
|  | 00D01E | System output voltage is higher than EV battery maximum voltage | 1 | V | 1. Use another DCWB to do charging. To tell the problem is related to EV or charger 2. Duplicate the failure symptom and record the CAN data via PCAN at the same time. (if available) 3. Provide the log file and PCAN file to BU service for further action. | N/A |  |  | Y | Y
|  | 00D01F | Permission on or H102.5.0 = 1 before CAN message received. | 1 | V | 1. Do charging again or use another EV to do charging test. To tell the problem is related to EV or charger 2. Duplicate the failure symptom and record the CAN data via PCAN at the same time. (if available) 3. Provide the log file and PCAN file to BU service for further action. | N/A |  |  | Y | Y
|  | 00D020 | Available output current (H108.3) < Minimum charger current (H100.0) | 1 | V
|  | 00D021 | Overload current protection | 1 | V
Note on E1: 作者: 1: Alarm 2: Warning 3: Notice

## Format
Alarm Code
Format:
| A | B | C | D | E | F
| Status | Dev ID | Cat. | Phase | Alarm Code
Status
0: Alarm 1: Recovery
Dev ID
0: Only 1 device Others: IDx
Cat.
|  | 4 | 5 |  | 6 | 7 | 8 |  | 9
|  | System | Communication |  | Network | SMR | Aux Power |  | GFD
|  | A | B |  | C | D |  | E
|  | Switch | Firmware Update |  | CCS | CHAdeMO |  | GB
Phase
Base on category to define
Alarm Code
Events and from 0-9 to A-Z
Group:
System | Status | Dev ID | 4 - B | 0 | Alarm Code
CCS | Status | Dev ID | C | Phase | Alarm Code
|  |  |  | 0 | Old
|  |  |  | 1 | V2G comm error
|  |  |  | 2 | System stop charging
|  |  |  | 3 | EV stop charging
CHAdeMO | Status | Dev ID | D | Phase | Alarm Code
|  |  |  | 0 | Old
|  |  |  | 1 | CHAdeMO Comm error
|  |  |  | 2 | System stop charging
|  |  |  | 3 | EV stop charging
System Log
Format:
YYYY.MM.DD HH.MM.SS - [Task name][Line] Information
Line: is 5 digital numbers in Dec(e.g 00123)

## Severity define
Severity | 1. Alarm | 2. Warning | 3. Notice
Can charging or not | No | Yes | Case by case
Characteristic | Hardware is failed or is a trigger | Something wrong in hardware or communication. (Not necessarily a malfunction) | a). Prompt b). Make a record c). Conditional mismatch d). Signal from the EV
Prompt time | Standby / Under charging | Standby / Under charging | Under charging / After charging
Countermeasure | Need to replace failed parts, and then the alarm will be removed | Need to troubleshooting, and then the warning will be removed | Automatically cleared after appearing once
Example | a). Module is failed b). Emergency button is pressed | a). No network connection b). Filter needs to be replaced c). Backend is disconnected | a). Authorization is fail b). Charging complete c). Stop command from EV

## SystemLog
Cat. | Loc. | Alarm code | Description | System Log | Note | Discuss
|  | 004001 | System input voltage is higher than workable range | 1. Alarm: Date - [Button][Line] Input OVP Lx:%dV > 310V 2. Recovery: Date - [Button][Line] Input OVP recovery L1:%dV, L2:%dV, L3:%dV < 300V
|  | 004002 | System input voltage (L1, L2 or L3) is lower than workable range | 1. Alarm: Date - [Button][Line] Input UVP Lx:%dV < 165V 2. Recovery: Date - [Button][Line] Input UVP recovery L1:%dV, L2:%dV, L3:%dV > 175V
|  | 004003 | System output voltage is higher than EV battery maximum voltage | Separate into CCS(Checking) and 00D01E [CHAdeMO] 1. Alarm: Charging && (Output voltage > (Threshold voltage + 5)) 2. Recvoery: End charging session 3. Trip time: 1 count 4. Sampling: while loop [CCS]
|  | 004004 | Request output current from EV is higher than present EVSE ability | Separate into CCS(Checking) and 00D00E [CHAdeMO] 1. Alarm: Charging && (Request output current > available current) 2. Recovery: End charging session 3. Trip time: 10s (Available current changed), 1 count (Normal) 4. Sampling: while loop [CCS]
|  | 004005 | Temperature of air inlet or input contactor is higher than workable range | 1. Alarm: [Air inlet] Date - [Button][Line] Air inlet temp too high: %d > 60 degree [AC contactor] Date - [Button][Line] AC contactor temp too high: %d > 80 degree 2. Recovery: [Air inlet] Date - [Button][Line] Air inlet temp too high recovery: %d <= 50 degree [AC contactor] Date - [Button][Line] AC contactor temp too high recovery: %d < 70 degree | 有Bug, Air inlet觸發OTP但AC contactor累積過一次之後溫度恢復正常, OTP會被清除
|  | 004006 | Temperature of CCS combo charging plug is higher than workable range | 1. Alarm: Date - [Comm2Csu][Line] CCS plug temp OTP: Byte33:%d 2. Recovery: Date - [Comm2Csu][Line] CCS plug temp OTP recovery: Byte33:%d
|  | 004007 | Air filters need to be replaced | 1. Alarm: Date - [Button][Line] Filter should be replaced 2. Recovery: Date - [Button][Line] Filter is replaced and ready
|  | 004008 | System fan error | When Duty command == 0 1. Alarm: Date - [Button][Line] System fan broken: duty:%d, Fan rpm:%d > Check rpm:500 2. Recovery: Date - [Button][Line] System fan broken recovery: duty:%d, Fan rpm:%d <= Check rpm:500 When Duty command != 0 1. Alarm: Date - [Button][Line] System fan broken: duty:%d, Fan rpm:%d < Check rpm:%d 2. Recovery: Date - [Button][Line] System fan broken recovery: duty:%d, Fan rpm:%d >= Check rpm:%d | CheckRPM: Ref to FW spec
|  | 004009 | System Init Failed | 1. Alarm: Date - [Task][Line] System init failed:%s 2. Recovery: N.A. | %s: Shared memory, Open, Malloc, Read or Parsing
|  | 00400A | Emergency button is pressed | 1. Alarm: Date - [Button2][Line] Emergency button pressed 2. Recovery: Date - [Button2][Line] Emergency button released
|  | 00400B | User authorized by backend is failed
|  | 00400C | User authorized by EVSE is failed
|  | 00400D | Temperature sensor of air inlet is broken | 1. Alarm: Date - [FanPWRCtrlFun][Line] Air inlet temp sensor broken: ADC_mV:%d 2. Recovery: Date - [FanPWRCtrlFun][Line] Air inlet temp sensor broken recovery: ADC_mV:%d
|  | 00400E | Temperature sensor of input contactor is broken | 1. Alarm: Date - [FanPWRCtrlFun][Line] AC contactor temp sensor broken: ADC_mV:%d 2. Recovery: Date - [FanPWRCtrlFun][Line] AC contactor temp sensor broken recovery: ADC_mV:%d
|  | 00400F | SPD trigger | 1. Alarm: Date - [Button][Line] SPD trigger 2. Recovery: Date - [Button][Line] SPD trigger recovery
|  | 004010 | Output fuse on CCS relay board is broken | 1. Alarm: Date - [main][Line] Output fuse CCS broken: SMR Vout:%dV, Relay Vfront:%dV 2. Recovery: N.A.
|  | 004011 | Output fuse on CHAdeMO relay board is broken | 1. Alarm: Date - [main][Line] Output fuse CHAdeMO broken: SMR Vout:%dV, Relay Vfront:%dV 2. Recovery: N.A.
|  | 004012 | Temperature sensor of CCS combo charging plug is broken | 1. Alarm: Date - [Comm2Csu][Line] CCS plug temp sensor broken; Byte33:%d 2. Recovery: Date - [Comm2Csu][Line] CCS plug temp sensor broken recovery; Byte33:%d
|  | 004013 | Temperature of air inlet or input contactor is lower than workable range | 1. Alarm: Date - [Button][Line] Air inlet temp too low: %d <= -40 degree 2. Recovery: Date - [Button][Line] Air inlet temp too low recovery: %d > -35 degree
|  | 004015 | The plug-in times of CCS charging plug is more than 10000 times | 1. Alarm: Date - [Button][Line] CCS plug-in over max times(%d): %d counts 2. Recovery: Date - [Button][Line] CCS plug-in over max times(%d) recovery: %d counts
|  | 004016 | The plug-in times of CHAdeMO charging plug is more than 10000 times | 1. Alarm: Date - [Button][Line] CHAdeMO plug-in over max times(%d): %d counts 2. Recovery: Date - [Button][Line] CHAdeMO plug-in over max times(%d) recovery: %d counts
|  | 004017 | System is timeout if user doesn't plug-in in 3 mnutes after authorized => Action item shall add check gun | 1. Alarm: Date - [main][Line] Connector plug-in timeout: %ds 2. Recovery: N.A.
|  | 004018 | Charging time is up | 1. Alarm: Date - [EvCan][Line] Charging time is up 2. Recovery: N.A.
|  | 004019 | System data storage is not enough.(不明確, 需要修改)
|  | 004020 | Unknow error
|  | 004021 | Charging is remotely stopped by backend office | 1. Alarm: [OCPP16J] Date - [main][Line] Remote stop by backend(OCPP16J) [OCPP15S] Date - [DeltaOCPP][Line] Remote stop by backend(OCPP15S) 2. Recovery: N.A. | Backend OCPP15S, OCPP16J
|  | 004022 | Input voltage is drop (L1) | 1. Alarm: Date - [Button2][Line] Input voltage drop L1 2. Recovery: Date - [Button2][Line] Input voltage drop recovery L1
|  | 004023 | System input voltage (L1) is lower than workable range
|  | 004024 | System reach stop SoC | 1. Alarm: Date - [main][Line] System reach stop SoC: %d% 2. Recovery: N.A.
|  | 004025 | System reach stop energy | 1. Alarm: Date - [main][Line] System reach stop Energy: %d kWh 2. Recovery: N.A.
|  | 005001 | Communication with CHAdeMO EV is broken | Separate into 00D00F, 00D011 1. Alarm: Communication is not built && (Permission is on ¦¦ (EV[102].5.1 == 1)) 2. Recovery: End charging session 3. Trip time: 1 count 4. Sampling: while loop 1. Alarm: Communication is not built 2. Recovery: End charging session 3. Trip time: 6s 4. Sampling: while loop 1. Alarm: D1 On && Communication is built && Can't receive EV CAN message 2. Recovery: End charging session 3. Trip time: 5s 4. Sampling: while loop
|  | 005005 | Communication with CCS EV is broken | Separate into 00C100 - 00C10D 1. Alarm: (Communicating ¦¦ Lock Connector ¦¦ Isolation Test) && (V2G Error ¦¦ DIN Comm End ¦¦ DIN Comm Standby ¦¦ Pilot State A) 2. Recovery: End charging session 3. Trip time: 1 count 4. Sampling: while loop
|  | 005006 | Power rectifier is broken | 1. Alarm: [Init] Date - [SmrCan][Line] setsockopt is failed [No response] Before charging start Date - [SmrCan][Line] No SMR in operation; AC contactor1:%d, AC contactor2:%d During charging [SmrCan][%d]main:#1 - No ping acknowledge, SHRMEM_RECTIFIER1_RELAY=%d, SHRMEM_RECTIFIER2_RELAY=%d 2. Recovery: N.A.
|  | 005007 | Communication with CCS controller is broken | 1. Alarm: Date - [Comm2Csu][Line] BA and CA comm failed: RX len:%d, Data:0x%x 0x%x 0x%x 0x%x 0x%x 0x%x 0x%x 0x%x 2. Recovery: Date - [Comm2Csu][Line] BA and CA communication failed recovery
|  | 005008 | Communication with auxiliary power module is broken | 1. Alarm: Date - [Comm2RelayBoard][Line] BA and aux board comm failed: RX len:%d, Data:0x%x 0x%x 0x%x 0x%x 0x%x 0x%x 2. Recovery: Date - [Comm2RelayBoard][Line] BA and aux board comm failed recovery
|  | 005009 | Communication with relay control module is broken | 1. Alarm: Date - [Comm2RelayBoard][Line] BA and relay board comm failed: RX len:%d, Data:0x%x 0x%x 0x%x 0x%x 0x%x 0x%x 2. Recovery: Date - [Comm2RelayBoard][Line] BA and relay board comm failed recovery
|  | 00500C | Communication with display module is broken | 1. Alarm: Date - [main][Line] BA and LCM comm failed 2. Recovery: Date - [main][Line] BA and LCM comm failed recovery
|  | 00500D | Communication with RFID module is broken | 1. Alarm: Date - [main][Line] BA and RFID module comm failed 2. Recovery: Date - [main][Line] BA and RFID module comm failed recovery
|  | 00500E | 3G module is not ready (module itself or SIM) | 1. Alarm: Date - [3gModem][Line] 3G module not exist 2. Recovery: Date - [3gModem][Line] 3G module exist
|  | 00500F | WiFi module is not ready |  | No wifi model
|  | 006001 | 3G connection is disconnected from APN | 1. Alarm: Date - [3gModem][Line] 3G APN disconnected 2. Recovery: Date - [3gModem][Line] 3G APN connnected
|  | 006002 | 3G connection is disconnected from internet | 1. Alarm: Date - [3gModem][Line] 3G internet disconnected 2. Recovery: Date - [3gModem][Line] 3G internet connnected
|  | 006003 | 3G connection is disconnected from backend office | 1. Alarm: Date - [main][Line] 3G backend disconnected 2. Recovery: Date - [main][Line] 3G backend connnected
|  | 006008 | Ethernet connection is disconnected from internet | Function not implement
|  | 006009 | Ethernet connection is disconnected from backend office | 1. Alarm: Date - [main][Line] Ethernet backend disconnected 2. Recovery: Date - [main][Line] Ethernet backend connnected
|  | 007001 | Power rectifier is abnormal | 1. Alarm: (One of below is possiblely shown in log file) Date - [SmrCan][Line]main:#%d - SMR latched by hardware defect Date - [SmrCan][Line]main:#%d - SMR latched by PFC defect Date - [SmrCan][Line]main:#%d - SMR latched by DCDC defect Date - [SmrCan][Line]main:#%d - SMR latched by unknow Date - [SmrCan][Line]main:#%d - SMR latched by Converter Date - [SmrCan][Line]main:#%d - SMR latched by output Fuse blown Date - [SmrCan][Line]main:#%d - SMR latched by input Fuse blown Date - [SmrCan][Line]main:#%d - SMR latched by output power too high 2. Recovery: N/A | 1. main:#%d means SMR CAN ID.
|  | 007002 | Input voltage of power rectifier is higher than workable range | 1. Alarm: (One of below is possiblely shown in log file) Date - [SmrCan][Line]main:#%d - SMR input voltage too high Date - [SmrCan][Line]main:#%d - One line outside range Date - [SmrCan][Line]main:#%d - Two lines outside range 2. Recovery: N/A
|  | 007003 | Input voltage of power rectifier is lower than workable range | 1. Alarm: Date - [SmrCan][Line]main:#%d - SMR input voltage too low 2. Recovery: N/A
|  | 007004 | Output voltage is higher than workable range of power rectifier | 1. Alarm: (One of below is possiblely shown in log file) Date - [SmrCan][Line]main:#%d - Temporary OVP Date - [SmrCan][Line]main:#%d - SMR latched by OVP 2. Recovery: N/A
|  | 007005 | Output voltage is lower than workable range of power rectifier | N/A
|  | 007006 | The temperature of air inlet in power rectifier is higher than workable range | 1. Alarm: (One of below is possiblely shown in log file) Date - [SmrCan][Line]main:#%d - Temporary OTP Date - [SmrCan][Line]main:#%d - SMR latched by OTP 2. Recovery: N/A
|  | 007007 | The temperature of air inlet in power rectifier is lower than workable range | N/A
|  | 007008 | The temperature of PFC is higher than workable range | N/A
|  | 007009 | The temperature of PFC is lower than workable range | N/A
|  | 00700A | The temperature of DCDC is higher than workable range | N/A
|  | 00700B | The temperature of DCDC is lower than workable range | N/A
|  | 00700C | The fan inside power rectifier is broken | 1. Alarm: (One of below is possiblely shown in log file) Date - [SmrCan][Line]main:#%d - SMR fan NG Date - [SmrCan][Line]main:#%d - SMR latched by fan NG 2. Recovery: N/A
|  | 00700D | Output oring diod is broken | N/A
|  | 00700E | Isolation test is failed |  | Separate to CCS and CHAdeMO group Function implement but alarm code is not used 1. [CHAdeMO] send 109.5.5 = 1(stop charging) and 109.5.1 = 1(Charger error) to EV. and system maybe show "Isolation test" after timeout 180s 2. [CCS] isolation test timeout, display maybe show 005005(CommCcsEvError) [CCS] N.A. [CHAdeMO][0.9] 1. Alarm: Isolation Test && (Vout < (Target Voltage - 20V)) && Vout > 10V && SMR Vout > 10V && Iout < 2A 2. Recovery: End charging session 3. Trip time: 10s(Alarm), 1 counts(Recovery) 4. Sampling: while loop [CHAdeMO][1.2] 1. Alarm: Isolation Test && (Vout < (Target Voltage - 20V)) && Iout < 1A 2. Recovery: End charging session 3. Trip time: 10s(Alarm), 1 counts(Recovery) 4. Sampling: while loop
|  | 008003 | 5 volt for system controller is higher than workable range | 1. Alarm: Date - [Comm2RelayBoard][Line] Aux Pow 5V_CSU OVP trigger 2. Recovery: Date - [Comm2RelayBoard][Line] Aux Pow 5V_CSU OVP recover
|  | 008004 | 5 volt for other system modules is higher than workable range | 1. Alarm: Date - [Comm2RelayBoard][Line] Aux Pow 5V_SYS OVP trigger 2. Recovery: Date - [Comm2RelayBoard][Line] Aux Pow 5V_SYS OVP recover
|  | 008005 | 5 volt for CAN bus is higher than workable range | 1. Alarm: Date - [Comm2RelayBoard][Line] Aux Pow 5V_CAN OVP trigger 2. Recovery: Date - [Comm2RelayBoard][Line] Aux Pow 5V_CAN OVP recover
|  | 008006 | 12 volt for other system modules is higher than workable range | 1. Alarm: Date - [Comm2RelayBoard][Line] Aux Pow 12V_SYS OVP trigger 2. Recovery: Date - [Comm2RelayBoard][Line] Aux Pow 12V_SYS OVP recover
|  | 008007 | 12 volt for EV communication is higher than workable range | 1. Alarm: Date - [Comm2RelayBoard][Line] Aux Pow 12V_EV OVP trigger 2. Recovery: Date - [Comm2RelayBoard][Line] Aux Pow 12V_EV OVP recover
|  | 008008 | 24 volt for relay control is higher than workable range | 1. Alarm: Date - [Comm2RelayBoard][Line] Aux Pow 24V OVP trigger 2. Recovery: Date - [Comm2RelayBoard][Line] Aux Pow 24V OVP recover
|  | 008009 | 5 volt for system controller is lower than workable range | 1. Alarm: Date - [Comm2RelayBoard][Line] Aux Pow 5V_CSU UVP trigger 2. Recovery: Date - [Comm2RelayBoard][Line] Aux Pow 5V_CSU UVP recover
|  | 00800A | 5 volt for other system modules is lower than workable range | 1. Alarm: Date - [Comm2RelayBoard][Line] Aux Pow 5V_SYS UVP trigger 2. Recovery: Date - [Comm2RelayBoard][Line] Aux Pow 5V_SYS UVP recover
|  | 00800B | 5 volt for CAN bus is lower than workable range | 1. Alarm: Date - [Comm2RelayBoard][Line] Aux Pow 5V_CAN UVP trigger 2. Recovery: Date - [Comm2RelayBoard][Line] Aux Pow 5V_CAN UVP recover
|  | 00800C | 12 volt for other system modules is lower than workable range | 1. Alarm: Date - [Comm2RelayBoard][Line] Aux Pow 12V_SYS UVP trigger 2. Recovery: Date - [Comm2RelayBoard][Line] Aux Pow 12V_SYS UVP recover
|  | 00800D | 12 volt for EV communication is lower than workable range | 1. Alarm: Date - [Comm2RelayBoard][Line] Aux Pow 12V_EV UVP trigger 2. Recovery: Date - [Comm2RelayBoard][Line] Aux Pow 12V_EV UVP recover
|  | 00800E | 24 volt for relay control is lower than workable range | 1. Alarm: Date - [Comm2RelayBoard][Line] Aux Pow 24V UVP trigger 2. Recovery: Date - [Comm2RelayBoard][Line] Aux Pow 24V UVP recover
|  | 008010 | The output current of 5 volt for system controller is higher than workable range | N/A
|  | 008011 | The output current of 5 volt for other system modules is higher than workable range | N/A
|  | 008012 | The output current of 5 volt for CAN bus is higher than workable range | N/A
|  | 008013 | The output current of 12 volt for other system modules is higher than workable range | N/A
|  | 008014 | The output current of 12 volt for EV communication is higher than workable range | N/A
|  | 008015 | The output current of 24 volt for relay control is higher than workable range | N/A
|  | 008016 | The temperature of 12 volt for EV communication is higher than workable range | N/A
|  | 008017 | The temperature of 5 volt for other system modules is higher than workable range | N/A
|  | 008018 | The temperature of 24 volt for relay control is higher than workable range | N/A
|  | 008019 | The ambinet temperature of auxiliary power is higher than workable range | 1. Alarm: [Comm2RelayBoard][Line] Aux Pow ambient OTP trigger 2. Recover: [Comm2RelayBoard][Line] Aux Pow ambient OTP recover
|  | 009001 | GFD trigger | 1. Alarm: Date - [Comm2RelayBoard][Line] GFD trigger; Vout:%dV 2. Recovery: Date - [Comm2RelayBoard][Line] GFD trigger recovery; Vout:%dV
|  | 009003 | GFD pre-warnning | 1. Alarm: Date - [Comm2RelayBoard][Line] GFD pre-warning; Vout:%dV 2. Recovery: Date - [Comm2RelayBoard][Line] GFD pre-warning recovery; Vout:%dV
|  | 009004 | GFD self-test fail | 1. Alarm: Date - [Comm2RelayBoard][Line] GFD self-test failed; Vout:%dV, GFD1:%dOmh, GFD2:%dOmh 2. Recovery: Date - [Comm2RelayBoard][Line] GFD self-test failed recovery; Vout:%dV, GFD1:%dOmh, GFD2:%dOmh
|  | 00A001 | Input contactor 1 is welding | 1. Alarm: Date - [main][Line] Input contactor 1 welding; AC contactor status:%d, DCWBVin1:%dV, DCWBVin2:%dV, DCWBVin3:%dV, SMRVin1:%dV, SMRVin2:%dV, SMRVin3:%dV 2. Recovery: N.A.
|  | 00A002 | Input contactor 1 is drived fault | 1. Alarm: Date -[main][Line] Input contactor 1/2 driving fault; AC contactor status:%d, SMR quantity:%d 2. Recovery: N.A.
|  | 00A003 | Input contactor 2 is welding | 1. Alarm: Date - [main][Line] Input contactor 2 welding; AC contactor status:%d, DCWBVin1:%dV, DCWBVin2:%dV, DCWBVin3:%dV, SMRVin1:%dV, SMRVin2:%dV, SMRVin3:%dV 2. Recovery: N.A.
|  | 00A004 | Input contactor 2 is drived fault | 1. Alarm: Date -[main][Line] Input contactor 1/2 driving fault; AC contactor status:%d, SMR quantity:%d 2. Recovery: N.A.
|  | 00A005 | The positive side of output relay for CCS charging is welding | 1. Alarm: Date - [main][Line] Pside of output relay for CCS control failed(Off); Cmd:%d, Response:%d 2. Recovery: N.A.
|  | 00A006 | The positive side of output relay for CCS charging is drived fault | 1. Alarm: Date - [main][Line] Pside of output relay for CCS control failed(On); Cmd:%d, Response:%d 2. Recovery: N.A.
|  | 00A007 | The positive side of output relay for CHAdeMO charging is welding | 1. Alarm: Date - [main][Line] Pside of output relay for CHAdeMO control failed(Off); Cmd:%d, Response:%d 2. Recovery: N.A.
|  | 00A008 | The positive side of output relay for CHAdeMO charging is drived fault | 1. Alarm: Date - [main][Line] Pside of output relay for CHAdeMO control failed(On); Cmd:%d, Response:%d 2. Recovery: N.A.
|  | 00A009 | The negative side of output relay for CCS charging is welding | 1. Alarm: Date - [main][Line] Nside of output relay for CCS control failed(Off); Cmd:%d, Response:%d 2. Recovery: N.A.
|  | 00A00A | The negative side of output relay for CCS charging is drived fault | 1. Alarm: Date - [main][Line] Nside of output relay for CCS control failed(On); Cmd:%d, Response:%d 2. Recovery: N.A.
|  | 00A00B | The negative side of output relay for CHAdeMO charging is welding | 1. Alarm: Date - [main][Line] Nside of output relay for CHAdeMO control failed(Off); Cmd:%d, Response:%d 2. Recovery: N.A.
|  | 00A00C | The negative side of output relay for CHAdeMO charging is drived fault | 1. Alarm: Date - [main][Line] Nside of output relay for CHAdeMO control failed(On); Cmd:%d, Response:%d 2. Recovery: N.A.
|  | 00A00D | The output relay for CCS charging is welding | 1. Alarm: Date - [main][Line] Output relay for CCS welding; Relay front volt:%dV, Relay back volt:%dV 2. Recovery: N.A.
|  | 00A00E | The output relay for CCS charging is drived fault | 1. Alarm: Date - [main][Line] Output relay for CCS driving fault; Relay front volt:%dV, Relay back volt:%dV 2. Recovery: N.A.
|  | 00A00F | The output relay for CHAdeMO charging is welding | 1. Alarm: Date - [main][Line] Output relay for CHAdeMO welding; Relay front volt:%dV, Relay back volt:%dV 2. Recovery: N.A. | Fn: Multiple functions
|  | 00A010 | The output relay for CHAdeMO charging is drived fault | 1. Alarm: Date - [main][Line] Output relay for CHAdeMO driving fault; Relay front volt:%dV, Relay back volt:%dV 2. Recovery: N.A. | Fn: Multiple functions
|  | 00A011 | The output pre-charge relay for CCS charging is welding | 1. Alarm: Date - [main][Line] Output pre-relay for CCS welding; Pre-relay front volt:%dV, Pre-relay back volt:%dV 2. Recovery: N.A.
|  | 00A012 | The output pre-charge relay for CCS charging is drived fault | 1. Alarm: Date - [main][Line] Output pre-relay for CCS driving fault; Pre-relay front volt:%dV, Pre-relay back volt:%dV 2. Recovery: N.A.
|  | 00A013 | CCS pilot line is broken | 1. Alarm: Date - [ErrorHandle][Line] CCS pilot line broken; Proximity:%d, Pilot state:%d 2. Recovery: N.A.
|  | 00A014 | CCS proximity is broken | 1. Alarm: Date - [ErrorHandle][Line] CCS proximity broken; Proximity:%d, Pilot state:%d 2. Recovery: N.A.
|  | 00B001 | The firmware update of auxiliary power module is failure | 1. Alarm: Date - [Comm2RelayBoard][Line] FW update of aux power failed:%s Date - [main][Line] FW update of aux power failed:Update time out 2. Recovery: N.A. | %s: Malloc failed,Open failed, Read image failed, Enter update FW failed, Comm failed or FlashBuild failed
|  | 00B002 | The firmware update of relay control module is failure | 1. Alarm: Date - [Comm2RelayBoard][Line] FW update of relay board failed:%s Date - [main][Line] FW update of relay board failed:Update time out 2. Recovery: N.A. | %s: Malloc failed,Open failed, Read image failed, Enter update FW failed, Comm failed or FlashBuild failed
|  | 00B003 | The firmware update of LCM module is failure | 1. Alarm: Date - [main][Line] FW update of LCM failed:%s 2. Recovery: N.A. | %s: Malloc failed,Malloc failed(Retrieve), Open failed, Read image failed, Update data failed,Enter update FW failed, Comm failed, Connect PIC failed, LCM erase failed or LCM verify failed
|  | 00B004 | The firmware update of CCS charging module is failure | 1. Alarm: Date - [Comm2Csu][Line] FW update of CCS board failed:%s Date - [main][Line] FW update of CCS board failed:Update time out 2. Recovery: N.A. | %s: Update time out, Malloc failed, Open failed, Read image failed, zip file failed, Image check sum failed, Enter update FW failed(timeout), Enter update FW failed(ack wrong), Comm failed(Remaining size wrong) ,Comm failed(Timeout), Update data failed(Length Error), Image Check sum failed(Ack) , File broken(Ack),FlashBuild timeout or FlashBuild failed
|  | 00B005 | The firmware update of CHAdeMO charging module is failure | 1. Alarm: Date - [main][Line] FW update of CHAdeMO board kernel failed:%s Date - [main][Line] FW update of CHAdeMO board rootf failed:%s 2. Recovery: N.A. | %s 1. Read image failed: Open failed ¦¦ Malloc failed ¦¦ Read length is different with image ¦¦ Not compatible ¦¦ Checksum error 2. Write data length error Open flash block failed(Write) ¦¦ Write length is not 0xCF0000 3. Data check error: Open flash block failed(Check) ¦¦ malloc failed(Check) ¦¦ Read length is not 0xCF0000 ¦¦ R/W checksum is different ¦¦ R/W checksum is different over 2 times)
|  | 00B006 | The firmware update of power converter module is failure | 1. Alarm: Primary: Date - [SmrCan][Line]SMR:#%d - FW update primary NG Date - [main][Line] FW update of SMR primary failed:Update time out Secondary: Date - [SmrCan][Line] SMR:#%d - FW update secondary failed:%s Date - [main][Line] FW update of SMR secondary failed:Update time out 2. Recovery: N.A. | %s: Malloc failed, Open failed, Read image failed, Enter update FW failed, Comm failed
|  | 00C001 | PLC module for CCS charging is broken | Function not implement
|  | 00C002 | CCS1 proximity is disconnected | 1. Alarm: Date - [Comm2Csu][Line][EV] CCS proximity disconnected; Proximity:%d, Pilot state:%s(%d) 2. Recovery: N.A.
|  | 00C003 | stop charging by CCS EV | Separate into 00C300 - 00C317 1. Alarm: CCS Charging && (PLC error ¦¦ DIN end ¦¦ Pilot B2, B1, A, Error) 2. Recovery: End charging
…
|  | 00C100 | SLAC - No data | 1. Alarm: Date - [Comm2Csu][Line] SLAC No PLC data(0x%02X%02X%02X%02X); Phase:%s, SLAC:0x%02X%02X, Error:%s 2. Recovery: N.A.
|  | 00C101 | SLAC error | 1. Alarm: Date - [Comm2Csu][Line] SLAC error(0x%02X%02X%02X%02X); Phase:%s, SLAC:0x%02X%02X, Error:%s 2. Recovery: N.A.
|  | 00C102 | SDP error | 1. Alarm: Date - [Comm2Csu][Line] SDP error(0x%02X%02X%02X%02X); Phase:%s, Error:%s 2. Recovery: N.A.
|  | 00C103 | TCP error | 1. Alarm: Date - [Comm2Csu][Line] TCP error(0x%02X%02X%02X%02X); Phase:%s, Error:%s 2. Recovery: N.A.
|  | 00C104 | V2G error - Idle | 1. Alarm: Date - [Comm2Csu][Line] V2G error(0x%02X%02X%02X%02X); Phase:%s, V2G:%s, Error:%s 2. Recovery: N.A.
|  | 00C105 | V2G error - supportedAppProtocol | 1. Alarm: Date - [Comm2Csu][Line] V2G error(0x%02X%02X%02X%02X); Phase:%s, V2G:%s, Error:%s 2. Recovery: N.A.
|  | 00C106 | V2G error - SessionSetup | 1. Alarm: Date - [Comm2Csu][Line] V2G error(0x%02X%02X%02X%02X); Phase:%s, V2G:%s, Error:%s 2. Recovery: N.A.
|  | 00C107 | V2G error - ServiceDiscovery | 1. Alarm: Date - [Comm2Csu][Line] V2G error(0x%02X%02X%02X%02X); Phase:%s, V2G:%s, Error:%s 2. Recovery: N.A.
|  | 00C108 | V2G error - ServicePaymentSelection | 1. Alarm: Date - [Comm2Csu][Line] V2G error(0x%02X%02X%02X%02X); Phase:%s, V2G:%s, Error:%s 2. Recovery: N.A.
|  | 00C109 | V2G error - ContractAuthentication | 1. Alarm: Date - [Comm2Csu][Line] V2G error(0x%02X%02X%02X%02X); Phase:%s, V2G:%s, Error:%s 2. Recovery: N.A.
|  | 00C10A | V2G error - ChargeParameterDiscovery | 1. Alarm: Date - [Comm2Csu][Line] V2G error(0x%02X%02X%02X%02X); Phase:%s, V2G:%s, Error:%s 2. Recovery: N.A.
|  | 00C10B | V2G error - CableCheck | 1. Alarm: Date - [Comm2Csu][Line] V2G error(0x%02X%02X%02X%02X); Phase:%s, V2G:%s, Error:%s 2. Recovery: N.A.
|  | 00C10C | V2G error - PreCharge | 1. Alarm: Date - [Comm2Csu][Line] V2G error(0x%02X%02X%02X%02X); Phase:%s, V2G:%s, Error:%s 2. Recovery: N.A.
|  | 00C10D | V2G error - PowerDelivery | 1. Alarm: Date - [Comm2Csu][Line] V2G error(0x%02X%02X%02X%02X); Phase:%s, V2G:%s, Error:%s 2. Recovery: N.A.
|  | 00C10E | V2G error - CurrentDemand | 1. Alarm: Date - [Comm2Csu][Line] V2G error(0x%02X%02X%02X%02X); Phase:%s, V2G:%s, Error:%s 2. Recovery: N.A.
00C10F
...
|  | 00C200 | Reserved
|  | 00C201 | Reserved
|  | 00C202 | Timeout error - ReadyToCharge | 1. Alarm: Date - [Comm2Csu][Line][EVSE] Timeout error - ReadyToCharge(0x%02X%02X%02X%02X); Pilot state:%s(%d), SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, EVSEPwrLimit:%dkW, EVSECurrLimit:%dA 2. Recovery: N.A.
|  | 00C203 | CableCheck error - SMR Vout is less than Vcmd | 1. Alarm: Date - [main][Line][EVSE] CableCheck error - SMR Vout(%dV) < 480V; SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, EVSEPwrLimit:%dkW, EVSECurrLimit:%dA 2. Recovery: N.A.
|  | 00C204 | CableCheck error - SMR Vout is over 20V | 1. Alarm: Date - [main][Line][EVSE] CableCheck error - SMR Vout(%dV) > 20V; SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, EVSEPwrLimit:%dkW, EVSECurrLimit:%dA 2. Recovery: N.A.
|  | 00C205 | CableCheck error - Output voltage is over 60V before insulation test | 1. Alarm: Date - [main][Line][EVSE] CableCheck error - Output voltage(%dV) > 60V before insulation test; Output relay status:%d, SMR output voltage:%dV 2. Recovery: N.A.
|  | 00C206 | CableCheck error - Output current is over 2A in insulation test | 1. Alarm: Date - [main][Line][EVSE] CableCheck error - Output current(%.1fA) > 2A; SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, EVSEPwrLimit:%dkW, EVSECurrLimit:%dA 2. Recovery: N.A.
|  | 00C207 | Precharge error - Output voltage is less than EV Vcmd | 1. Alarm: Date - [main][Line][EVSE] Precharge error - SMR Vout(%dV) < Target voltage(%dV); SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, EVSEPwrLimit:%dkW, EVSECurrLimit:%dA 2. Recovery: N.A.
|  | 00C208 | Precharge error - Output current is over 1.5A in precharge | 1. Alarm: Date - [main][Line][EVSE] Precharge error - Output current(%.1fA) > 1.5A; SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, EVSEPwrLimit:%dkW, EVSECurrLimit:%dA 2. Recovery: N.A.
00C209
...
|  | 00C300 | EV error - FAILED_RESSTemperatureInhibit | 1. Alarm: Date - [Comm2Csu][Line][EV] FAILED_RESSTemperatureInhibit(0x%02X%02X%02X%02X); SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, EVSEPwrLimit:%dkW, EVSECurrLimit:%dA 2. Recovery: N.A.
|  | 00C301 | EV error - FAILED_EVShiftPosition | 1. Alarm: Date - [Comm2Csu][Line][EV] FAILED_EVShiftPosition(0x%02X%02X%02X%02X) 2. Recovery: N.A.
|  | 00C302 | EV error - FAILED_ChargerConnectorLockFault | 1. Alarm: Date - [Comm2Csu][Line][EV] FAILED_ChargerConnectorLockFault(0x%02X%02X%02X%02X) 2. Recovery: N.A.
|  | 00C303 | EV error - FAILED_EVRESSMalfunction | 1. Alarm: Date - [Comm2Csu][Line][EV] FAILED_EVRESSMalfunction(0x%02X%02X%02X%02X); SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, EVSEPwrLimit:%dkW, EVSECurrLimit:%dA 2. Recovery: N.A.
|  | 00C304 | EV error - FAILED_ChargingCurrentdifferential | 1. Alarm: Date - [Comm2Csu][Line][EV] FAILED_ChargingCurrentdifferential(0x%02X%02X%02X%02X); SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, EVSEPwrLimit:%dkW, EVSECurrLimit:%dA 2. Recovery: N.A.
|  | 00C305 | EV error - FAILED_ChargingVoltageOutOfRange | 1. Alarm: Date - [Comm2Csu][Line][EV] FAILED_ChargingVoltageOutOfRange(0x%02X%02X%02X%02X); SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, EVSEPwrLimit:%dkW, EVSECurrLimit:%dA 2. Recovery: N.A.
|  | 00C306 | EV error - FAILED_Reserved_A | 1. Alarm: Date - [Comm2Csu][Line][EV] FAILED_Reserved_A(0x%02X%02X%02X%02X) 2. Recovery: N.A.
|  | 00C307 | EV error - FAILED_Reserved_B | 1. Alarm: Date - [Comm2Csu][Line][EV] FAILED_Reserved_B(0x%02X%02X%02X%02X) 2. Recovery: N.A.
|  | 00C308 | EV error - FAILED_Reserved_C | 1. Alarm: Date - [Comm2Csu][Line][EV] FAILED_Reserved_C(0x%02X%02X%02X%02X) 2. Recovery: N.A.
|  | 00C309 | EV error - FAILED_ChargingSystemIncompatibility | 1. Alarm: Date - [Comm2Csu][Line][EV] FAILED_ChargingSystemIncompatibility(0x%02X%02X%02X%02X); SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, EVSEPwrLimit:%dkW, EVSECurrLimit:%dA 2. Recovery: N.A.
|  | 00C30A | EV error - FAILED_NoData | 1. Alarm: Date - [Comm2Csu][Line][EV] FAILED_NoData(0x%02X%02X%02X%02X) 2. Recovery: N.A.
|  | 00C30B | Stop charging at supportedAppProtocol | 1. Alarm: Date - [Comm2Csu][Line][EV] Stop charging at supportedAppProtocol(0x%02X%02X%02X%02X); SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, EVSEPwrLimit:%dkW, EVSECurrLimit:%dA 2. Recovery: N.A.
|  | 00C30C | Stop charging at SessionSetup | 1. Alarm: Date - [Comm2Csu][Line][EV] Stop charging at SessionSetup(0x%02X%02X%02X%02X); SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, EVSEPwrLimit:%dkW, EVSECurrLimit:%dA 2. Recovery: N.A.
|  | 00C30D | Stop charging at ServiceDiscovery | 1. Alarm: Date - [Comm2Csu][Line][EV] Stop charging at ServiceDiscovery(0x%02X%02X%02X%02X); SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, EVSEPwrLimit:%dkW, EVSECurrLimit:%dA 2. Recovery: N.A.
|  | 00C30E | Stop charging at ServicePaymentSelection | 1. Alarm: Date - [Comm2Csu][Line][EV] Stop charging at ServicePaymentSelection(0x%02X%02X%02X%02X); SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, EVSEPwrLimit:%dkW, EVSECurrLimit:%dA 2. Recovery: N.A.
|  | 00C30F | Stop charging at ContractAuthentication | 1. Alarm: Date - [Comm2Csu][Line][EV] Stop charging at ContractAuthentication(0x%02X%02X%02X%02X); SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, EVSEPwrLimit:%dkW, EVSECurrLimit:%dA 2. Recovery: N.A.
|  | 00C310 | Stop charging at ChargeParameterDiscovery | 1. Alarm: Date - [Comm2Csu][Line][EV] Stop charging at ChargeParameterDiscovery(0x%02X%02X%02X%02X); SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, EVSEPwrLimit:%dkW, EVSECurrLimit:%dA 2. Recovery: N.A.
|  | 00C311 | Stop charging at CableCheck | 1. Alarm: Date - [Comm2Csu][Line][EV] Stop charging at CableCheck(0x%02X%02X%02X%02X); SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, EVSEPwrLimit:%dkW, EVSECurrLimit:%dA 2. Recovery: N.A.
|  | 00C312 | Stop charging at PreCharge | 1. Alarm: Date - [Comm2Csu][Line][EV] Stop charging at PreCharge(0x%02X%02X%02X%02X); SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, EVSEPwrLimit:%dkW, EVSECurrLimit:%dA 2. Recovery: N.A.
|  | 00C313 | Stop charging at CurrentDemand | 1. Alarm: Date - [Comm2Csu][Line][EV] Stop charging at CurrentDemand(0x%02X%02X%02X%02X); SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, EVSEPwrLimit:%dkW, EVSECurrLimit:%dA 2. Recovery: N.A.
|  | 00C314 | Stop charging at CurrentDemand by PowerDelivery(BulkChargingComplete) | 1. Alarm: Date - [Comm2Csu][Line][EV] Stop charging at CurrentDemand by PowerDelivery(BulkChargingComplete)(0x%02X%02X%02X%02X) 2. Recovery: N.A.
|  | 00C315 | Stop charging at CurrentDemand by PowerDelivery(ChargingComplete) | 1. Alarm: Date - [Comm2Csu][Line][EV] Stop charging at CurrentDemand by PowerDelivery(ChargingComplete)(0x%02X%02X%02X%02X) 2. Recovery: N.A.
|  | 00C316 | Stop charging by pilot A | 1. Alarm: Date - [Comm2Csu][Line][EV] Stop charging by pilot A(0x%02X%02X%02X%02X); Pilot state:%s(%d) 2. Recovery: N.A.
|  | 00C317 | Stop charging by pilot B | 1. Alarm: Date - [Comm2Csu][Line][EV] Stop charging by pilot B(0x%02X%02X%02X%02X); Pilot state:%s(%d), SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, EVSEPwrLimit:%dkW, EVSECurrLimit:%dA 2. Recovery: N.A.
|  | 00C318 | Stop charging by pilot E, F or error | 1. Alarm: Date - [Comm2Csu][Line][EV] Stop charging by pilot E, F or error(0x%02X%02X%02X%02X); Pilot state:%s(%d), SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, EVSEPwrLimit:%dkW, EVSECurrLimit:%dA 2. Recovery: N.A.
00C319
|  | 00D001 | No charging permission come from CHAdeMO EV | 1. Alarm: Date - [EvCan][Line][EV] No permission; Opto-coupler(j):%d, SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, CAN Data 2. Recovery: N.A. | Fn: Multiple functions CAN Data: \n\tEV100(Hex 0-7): %02x \n\tEV101(Hex 0-7): %02x \n\tEV102(Hex 0-7): %02x \n\tCP108(Hex 0-7): %02x \n\tCP109(Hex 0-7): %02x
|  | 00D002 | Battery malfunction come from CHAdeMO EV | Separate into 00D00D, 00D014, 00D016, 00D017, 00D018, 00D019 1. Alarm: (Target battery volt > Max battery volt) ¦¦ (ISO test start(Vreq=0) && EV contactor on) ¦¦ (ISO testing(Vreq=500) && Vout < 480V && time > 20s && I > 2A) ¦¦ (ISO tested(Vreq=0) && Vout > 20V && time > 35s) ¦¦ (ISO test complete && time > 11s && No Ireq) ¦¦ (Stop CHA && time > 7s && Vout > 10V) 2. Recovery: End charging
|  | 00D003 | Target battery voltage is higher than available output voltage | 1. Alarm: Date - [EvCan][Line][EVSE] CHG_MX(%dV) > LIMIT_V(%dV); CAN Data 2. Recovery: N.A. | CAN Data: refer to 00D001
|  | 00D004 | Battery undervoltage | 1. Alarm: Date - [EvCan][Line][EV] Battery undervoltage; SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, CAN Data 2. Recovery: N.A. | CAN Data: refer to 00D001
|  | 00D005 | Battery overvoltage | 1. Alarm: Date - [EvCan][Line][EV] Battery overvoltage; SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, CAN Data 2. Recovery: N.A. | CAN Data: refer to 00D001
|  | 00D006 | Present output current is different from target current | 1. Alarm: Date - [EvCan][Line][EV] Battery current deviation error; SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, CAN Data 2. Recovery: N.A. | CAN Data: refer to 00D001
|  | 00D007 | Battery OTP come from CHAdeMO EV | 1. Alarm: Date - [EvCan][Line][EV] High battery temperature; SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, CAN Data 2. Recovery: N.A. | CAN Data: refer to 00D001
|  | 00D008 | Present output voltage is different from target voltage | 1. Alarm: Date - [EvCan][Line][EV] Battery voltage deviation error; SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, CAN Data 2. Recovery: N.A. | CAN Data: refer to 00D001
|  | 00D009 | Position shift alarm is come from CHAdeMO EV | 1. Alarm: Date - [EvCan][Line][EV] Vehicle shift position; CAN Data 2. Recovery: N.A. | CAN Data: refer to 00D001
|  | 00D00A | EV other fault is come from CHAdeMO EV | 1. Alarm: Date - [EvCan][Line][EV] Charging system error; SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, CAN Data 2. Recovery: N.A. | CAN Data: refer to 00D001
|  | 00D00B | CHAdeMO connector lock is broken | 1. Alarm: Date - [EvCan][Line][EVSE] CHAdeMO connector lock is broken; Detect status:%d 2. Recovery: N.A. | Fn: Multiple functions
|  | 00D00C | CHAdeMO proximity disconnection | Function not implement
|  | 00D00D | Battery malfunction - Target battery voltage is higher than maximum battery voltage | 1. Alarm: Date - [EvCan][Line][EVSE] CHG_MX(%dV) > BAT_MX(%dV); CAN Data 2. Recovery: N.A. | CAN Data: refer to 00D001
|  | 00D00E | Charging current request is higher than available output current | 1. Alarm: Date - [EvCan][Line][EVSE] Target current(%dA) > Available current(%dA); CAN Data 2. Recovery: N.A. | Fn: Multiple functions CAN Data: refer to 00D001
|  | 00D00F | Timeout error - Start of Vehicle CAN data | 1. Alarm: Date - [EvCan][Line][EVSE] Timeout error - Start of Vehicle CAN data 2. Recovery: N.A. | Fn: Multiple functions
|  | 00D010 | Timeout error - CAN communication fault | 1. Alarm: Date - [EvCan][Line][EVSE] Timeout error - CAN communication fault 2. Recovery: N.A. | Fn: Multiple functions
|  | 00D011 | Timeout error - Charging enable | 1. Alarm: Date - [EvCan][Line][EVSE] Timeout error - Charging enable; SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, CAN Data 2. Recovery: N.A. | Fn: Multiple functions CAN Data: refer to 00D001
|  | 00D012 | Timeout error - EV contactor close | 1. Alarm: Date - [EvCan][Line][EVSE] Timeout error - EV contactor close; SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, CAN Data 2. Recovery: N.A. | Fn: Multiple functions CAN Data: refer to 00D001
|  | 00D013 | Timeout error - Charging current request | 1. Alarm: Date - [EvCan][Line][EVSE] Timeout error - Charging current request; SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, CAN Data 2. Recovery: N.A. | Fn: Multiple functions CAN Data: refer to 00D001
|  | 00D014 | Insulation error - SMR Vout is less than Vcmd | 1. Alarm: Date - [main][Line][EVSE] Insulation error - SMR Vout(%dV) < %dV(Target volt - 20V); SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA 2. Recovery: N.A. | Fn: Multiple functions CAN Data: refer to 00D001
|  | 00D015 | Insulation error - SMR Vout is over 20V | 1. Alarm: Date - [main][Line][EVSE] Insulation error - SMR Vout(%dV) > 20V; SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA 2. Recovery: N.A. | Fn: Multiple functions CAN Data: refer to 00D001
|  | 00D016 | Insulation error - Output voltage over 10V before insulation test | 1. Alarm: Date - [EvCan][Line][EVSE] Insulation error - Output voltage(%dV) > 10V before insulation test; Output relay status:0x%x, SMR Vout:%dV 2. Recovery: N.A. | Fn: Multiple functions
|  | 00D017 | Insulation error - Output voltage over 20V after insulation test | 1. Alarm: Date - [EvCan][Line][EVSE] Insulation error - Output voltage(%dV) > 20V after insulation test; SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA 2. Recovery: N.A. | Fn: Multiple functions
|  | 00D018 | Insulation error - Output current is over 2A in insulation test | 1. Alarm: Date - [main][Line][EVSE] Insulation error - Output current(%.1fA) > 2A; SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA 2. Recovery: N.A.
|  | 00D019 | Vehicle voltage error - Output voltage over 10V after charging | 1. Alarm: Date - [EvCan][Line][EVSE] Vehicle voltage error - Output voltage(%dV) > 10V after charging; Output relay status:0x%x, SMR Vout:%dV 2. Recovery: N.A. | Fn: Multiple functions
|  | 00D01A | Available current is less than Minimum charge current
|  | 00D01B | CHAdeMO system error - process | 1. Alarm: Date - [EvCan][Line][EVSE] CHAdeMO system error - process 2. Recovery: N.A.
|  | 00D01C | CHAdeMO EV permission disable time out after charging | 1. Alarm: Date - [EvCan][Line][EVSE] Timeout error - Permission off after charging; Opto-coupler(j):%d, CAN Data 2. Recovery: N.A.
|  | 00D01D | CHAdeMO EV contactor open time out after charging | 1. Alarm: Date - [EvCan][Line][EVSE] Timeout error - EV contactor open after charging; EV102.5:%d, CAN Data 2. Recovery: N.A.
|  | 00D01E | System output voltage is higher than EV battery maximum voltage | 1. Alarm: Date - [EvCan][Line][EVSE] Output OVP: Output voltage(%dV) > LIMIT_VOLT(%dV); SMR AvailPwr:%dW, SMR AvailCurr:%dA, Vcmd:%dV, Icmd:%dA, Vout:%dV, Iout:%dA, CAN Data 2. Recovery: N.A. | LIMIT_VOLT: min(Max battery volt, Available output volt) Fn: Multiple functions CAN Data: refer to 00D001
|  | 00D01F | Permission on or H102.5.0 = 1 before CAN message received. | 1. Alarm: Date - [EvCan][Line][EV] EV enable charging before sending CAN message; Opto-coupler(j):%d, CAN Data 2. Recovery: N.A. | CAN Data: refer to 00D001

## Generic Service Action
Failure Symptom Information.
Is it a single case? or also happened in another EV?
Is this failure symptom happened everytime? or irregular?
Is this failure symptom happened when start charging? or during charging (after charging few minutes)?
Is it about CCS charging or CHAdeMO charging?
Basic Inspection
Re-start DC Wallbox
Re-plug charging gun
Check the modules (SMR, Aux. Power, CHAdeMO CSU, CCS CSU) are screwed tightly on DC Wallbox. If executable, try to re-install these modules.
Check the each connectors on Relay Control Board are connection well. If executable, try to re-install the connectors on board.
Observe the LED status of SMR during charging (if executable)
Advanced
What is the FW version (find the answer in log file)
Update the FW to the newest version (by USB)
Download Wireshark file (which is the communication data during CCS charging)