## Alarm code list
DC Wallbox 25kw alarm code list for Delta front-end
|  | Delta confidential |  |  | Service part
Alarm code | Description | Condition | Contact BU Service if necessary | Action | PCB | PN
004001 | System input voltage is higher than workable range | 1. Alarm: Input voltage > 305Vac 2. Recovery: Input voltage < 290Vac |  | 1. Use multimeter to measure system input phase voltage that should less than 305V. 2. Check AC input voltage sense wire from input terminal bus bar to relay controller board. 3. Replace service part | 293408400X | Relay control board
004002 | System input voltage (L2 or L3) is lower than workable range | 1. Alarm: Input voltage(L2 or L3) < 170Vac 2. Recovery: Input voltage (L2 or L3)> 185Vac |  | 1. Use multimeter to measure system input phase voltage L2 and L3 higher 185V. 2. Check AC input voltage sense wire from input terminal bus bar to relay controller board. 3. If item 1 and item 2 are correction, replace service part | 293408400X | Relay control board
004003 | System output voltage is higher than EV battery maximum voltage | Output voltage > EV maximum battery voltage * 1.05 | V | 1. Retry 3 times, if still show this alarm, contact BU Service 2. Download log file and record EV make and model | x | N/A
004004 | Request output current from EV is higher than present EVSE ability | Request output current > available current + 1A | V | 1. Retry 3 times, if still show this alarm, contact BU Service 2. Download log file and record EV make and model | x | N/A
004005 | Temperature of air inlet or input contactor is higher than workable range | 1.Alarm: Air inlet > 60 degree C Input contactor > 80 degree C 2.Recovery: Air inlet < 50 degree C Input contactor < 70 degree C |  | 1. Check ambient temperature is higher than 60°C. 2. If ambient temperature is lower than 60°C, check cleanliness of air filter on both side. 3. Wait 30 minutes, then retry again. If alarm still appears in 3 minutes, the temperature sensor in the DC charger was shorted. Replace service part. | 293403820X | Temperature Sensor 091103PJ16
004006 | Temperature of CCS combo charging plug is higher than workable range | 1.Alarm: > 85 degree C 2.Recovery: < 75 degree C |  | 1.Confirm the charging gun temperature is higher than 85°C and check the cleanliness of charging gun contacts. 2. If charging gun temperature is lower than 85°C, wait 30 minutes then retry again. 3. If the alarm still appear in 3 minutes, the temperature sensor in the charging gun was shorted. Replace service part. | 293405620X Charging plug | CCS charging plug
004007 | Air filters need to be replaced | Delta Delta FW algorithm |  | 1. Check air filter cleanliness of both side. If the air filter was dirty, please change a new one. 2. If the air filter is clean, please retry again. 3. If the alarm still appear, please change parts as "service item". | 293409010X | Flow detect board
004008 | System fan speed too low | 1.Alarm: fan speed < fan speed cmd/2 2.Recovery: fan speed > fan speed cmd/2 |  | 1. Reboot charger 2. Tap card and check the system fan (system fan does not function when charger idle) 3. Replace service part |  | System fan 3620889311
004009 | Self test of system controller is fail |  | V | 1. Replace service part 2. If still failed after replace CHAdeMO CSU, download log file and contact BU Service | 2934038208 | CHAdeMO CSU
00400A | Emergency button is pressed | Delta FW algorithm |  | 1. Release emergency button 2. Check the contact of emergency button, replace it if opened. 3. If the contact of emergency button is closed, replace CHAdeMO CSU | 2934038208 | Emergency button CHAdeMO CSU
00400B | User authorized by backend is failed | User can not accepted by backend. |  | 1. Check with back office provider or confirm configuration file | x | N/A
00400C | User authorized by EVSE is failed | User's RFID card can not accepted by EVSE. |  | 1. Check with back office provider or confirm configuration file 2. Check the RFID card number is in local list | x | N/A
00400D | Temperature sensor of air inlet is broken | CSU BA detect temperature sensor's value less than -40°C or higher than 125°C. |  | 1. Check resistance of air inlet temperature sensor between 190kOhm ~ 2kOhm 2. If the temperature sensor was broken, please change temperature sensor. 3. If the temperature sensor was not broken, please change CHAdeMO CSU | 2934038208 | Temperature Sensor 091103PJ16 CHAdeMO CSU
00400E | Temperature sensor of input contactor is broken | CSU BA detect temperature sensor's value less than -40°C or higher than 125°C. |  | 1. Check resistance of air inlet temperature sensor between 190kOhm ~ 1kOhm 2. If the temperature sensor was broken, please change temperature sensor. 3. If the temperature sensor was not broken, please change CHAdeMO CSU | 2934038208 | Temperature Sensor 091103PJ16 CHAdeMO CSU
00400F | SPD trigger | Delta FW algorithm |  | 1. If the contact of SPD is closed, replace SPD board. 2. If the contact of SPD is open, check the wiring. 3. Replace CHAdeMO CSU | 2934038208 | SPD CHAdeMO CSU
004010 | Output fuse on CCS relay board is broken | 1.Alarm: SMR output voltage - SMR1 Output voltage before relay > 10V |  | 1. Replace service part |  | US model fuse: 0891170224 EU model fuse: 0891171003
004011 | Output fuse on CHAdeMO relay board is broken | 1.Alarm: SMR output voltage - SMR2 Output voltage before relay > 10V |  | 1. Replace service part |  | US model fuse: 0891170224 EU model fuse: 0891171003
004012 | Temperature sensor of CCS combo charging plug is broken | 1. CSU BA detect temperature sensor's value less than -40°C or higher than 125°C. |  | 1. Check resistance of CCS charging plug is between 842kOhm ~ 1480kOhm 2. If the temperature sensor is damaged, please change CCS charging plug 3. If the temperature sensor is not damaged, replaec CHAdeMO CSU |  | CCS charging plug CHAdeMO CSU
004013 | Temperature of air inlet or input contactor is lower than workable range | 1.Alarm: Air inlet < -40 degree C Input contactor < -40 degree C 2.Recovery: Air inlet > -30 degree C Input contactor > -30 degree C |  | 1.Confirm ambient temperature is lower than -40°C. 2.If ambient temperature higher than -40°C, check temperature sensor is close circuit 3.Replace service part |  | Temperature Sensor 091103PJ16
004015 | The plug-in times of CCS charging plug is more than 10000 times | 1. CCS plug over 10000 times |  | 1. Check clearance of CCS plug. 2. Suggest to replace CCS charging plug |  | CCS Charging plug
004016 | The plug-in times of CHAdeMO charging plug is more than 10000 times | 1. CHAdeMo plug over 10000 times |  | 1. Check clearance of CHAdeMO plug. 2. Suggest to replace CHAdeMO charging plug |  | CHAdeMO plug
004017 | System is timeout if user doesn't plug-in in 3 mnutes after authorized | 1.Alarm: unplug > 3 min (after authorized) |  | 1. plug-in charging gun in 3 mnutes after authorized | x | N/A
004018 | Charging time is up | 1.Charging time > 2hr (defult) |  | 1. Check charger time out 2. Update time out by configuration tool | x | N/A
004019 | System data storage is not enough. | BA CSU storage size: 32M bytes | V | 1. Replace CHAdeMO CSU 2. Contact BU Service | x | CHAdeMO CSU
004020 | Unknow error |  | V | 1. Contact BU Service | x | N/A
004021 | Charging is remotely stopped by backend office | 1.Receive stoptransaction from backend system |  | 1. Check with back office provider | x | N/A
004022 | Input voltage is drop (L1) | Delta FW algorithm |  | 1. Check power grid. | x | N/A
004023 | System input voltage (L1) is lower than workable range | 1. Alarm: Input voltage L1 < 170Vac 2. Recovery: Input voltage L1 > 185Vac |  | 1. Check input phase voltage higher than 185V. 2. Check AC input voltage sense wire from input terminal bus bar to relay controller board. 3. Replace service part | 293408400X | Relay control board
004024 | System reaches EVSE stop SoC | charging reaches EVSE stop SoC |  | normal stop, no service action |  | N/A
005001 | Communication with CHAdeMO EV is broken | Any CAN BUS message come from EV side over 100mSec. | V | 1. Check CHAdeMO plug wiring to DC wallbox is well. 2. Replace service part and contact BU Service |  | CHAdeMO charging plug CHAdeMO CSU
005005 | Communication with CCS EV is broken | Any PLC message come from EV side over 100mSec. | V | 1. Check CCS plug wiring to DC wallbox is well. 2. Replace service part and contact BU Service |  | CCS plug CHAdeMO CSU
005006 | Power rectifier is broken | CSU BA can not ping SMR. |  | When this alarm code appear, please follow below steps to check root cause: 1. Check AC input contactor can operated at starting charge process.If the contactor fail, replace AC contactor 2. Check LED on the SMR panel is light up. If the LED not light up, please change SMR 3. Check signal wire from SMR to back plane board |  | AC Contactor SMR
005007 | Communication with CCS controller is broken | CSU BA can not get message from UART interface to CSU CA. |  | 1. Check LED on CCS CSU. Replace CCS CSU if LEDs are not light on 2. Unplug and plug CCS CSU and CHAdeMO CSU, then, reboot system again. |  | CCS CSU
005008 | Communication with auxiliary power module is broken | CSU BA can not get message from RS-485 interface to auxiliary power module. |  | 1. Please check the RS-485 cable between relay control board and auxiliary power 2. Replug auxiliary power, then reboot system 3. Replace auxiliary power if the alarm code still appear |  | Auxiliary power
005009 | Communication with relay control module is broken | CSU BA can not get message from RS-485 interface to relay control module. |  | 1. Please check the RS-485 cable between back plane board and relay control board 2. Reboot system 3. Replace relay control board if the alarm code still appear |  | Relay control board
00500C | Communication with display module is broken | CSU BA can not get message from RS-232 interface to display module. |  | 1. Please check the RS-232 cable between back plane board and display module. 2. Reboot system 3. Replace display module if the alarm code still appear |  | LCM module
00500D | Communication with RFID module is broken | CSU BA can not get message from RS-232 interface to RFID module. |  | 1. Please check the RS-232 cable between back plane board and RFID module. 2. Reboot system 3. Replace 3G module if the alarm code still appear |  | RFID module
00500E | 3G module is not ready (module itself or SIM) |  |  | 1. Check LEDs on the 3G module is light on or not. Replace 3G module if the LEDs not light on. 2. If the LEDs are light on, check the SIM card. |  | 3G Module
00500F | WiFi module is not ready | No wifi model |  | N/A |  | N/A
006001 | 3G connection is disconnected from APN |  |  | 1. Check APN setting in the log file. 2. Reboot system again. |  | N/A
006002 | 3G connection is disconnected from internet |  |  | 1. Check internet status in the log file. 2. Check LEDs on the 3G module is light on or not. Replace 3G module if the LEDs not light on. 3. Reboot system again. |  | 3G Module
006003 | 3G connection is disconnected from backend office |  |  | 1. Check backend system status in the log file. 2. Reboot system again. |  | N/A
006008 | Ethernet connection is disconnected from internet |  |  | 1. Check internet status in the log file. 2. Reboot system again. |  | N/A
006009 | Ethernet connection is disconnected from backend office |  |  | 1. Check backend system status in the log file. 2. Reboot system again. |  | N/A
007001 | Hardware component in power rectifier is broken | 1.Receive from SMR |  | 1. Check LED on the SMR panel, if the LED color is red, please change the SMR. 2. If the LED color is green, please reboot system, then check again. |  | SMR
007002 | Input voltage of power rectifier is higher than workable range | 1.Receive from SMR |  | 1. Use multimeter to measure system input phase voltage, it should less than 305V. 2. Replace service part |  | SMR
007003 | Input voltage of power rectifier is lower than workable range | 1.Receive from SMR |  | 1. Use multimeter to measure system input phase voltage, it should higher than 90V. 2. Replace service part |  | SMR
007004 | Output voltage is higher than workable range of power rectifier | 1.Receive from SMR |  | 1. Use multimeter to measure system DC output voltage during cable check phase, it should less than 500V. 2. Replace service part |  | SMR
007006 | The temperature of air inlet in power rectifier is higher than workable range | 1.Receive from SMR |  | 1. Ambient temperature is higher than 50°C, keep charger at ventilated area 2. Replace service part |  | SMR
007008 | The temperature of PFC is higher than workable range | 1.Receive from SMR |  | 1. Ambient temperature is higher than 50°C, keep charger at ventilated area 2. Replace service part |  | SMR
007009 | The temperature of PFC is lower than workable range | 1.Receive from SMR |  | 1. Ambient temperature should higher than -40°C 2. Replace service part |  | SMR
00700A | The temperature of DCDC is higher than workable range | 1.Receive from SMR |  | 1. Ambient temperature is higher than 50°C, keep charger at ventilated area 2. Replace service part |  | SMR
00700B | The temperature of DCDC is lower than workable range | 1.Receive from SMR |  | 1. Ambient temperature should higher than -40°C 2. Replace service part |  | SMR
00700C | The fan inside power rectifier is broken | 1.Receive from SMR 2. Fan speed feedback value less than half of fan spped command. |  | 1. Please check there have any thing lock on SMR fan. 2. Replace service part |  | SMR
00700D | Output oring diod is broken | 1.Receive from SMR |  | 1. Replace service part |  | SMR
00700E | Isolation test is failed | 1.Receive from SMR |  | 1. Replace service part |  | SMR
008003 | 5 volt for system controller is higher than workable range | Delta FW algorithm |  | 1. Replace service part |  | Auxiliary power
008004 | 5 volt for other system modules is higher than workable range | Delta FW algorithm |  | 1. Replace service part |  | Auxiliary power
008005 | 5 volt for CAN bus is higher than workable range | Delta FW algorithm |  | 1. Replace service part |  | Auxiliary power
008006 | 12 volt for other system modules is higher than workable range | Delta FW algorithm |  | 1. Replace service part |  | Auxiliary power
008007 | 12 volt for EV communication is higher than workable range | Delta FW algorithm |  | 1. Replace service part |  | Auxiliary power
008008 | 24 volt for relay control is higher than workable range | Delta FW algorithm |  | 1. Replace service part |  | Auxiliary power
008009 | 5 volt for system controller is lower than workable range | Delta FW algorithm |  | 1. Replace service part |  | Auxiliary power
00800A | 5 volt for other system modules is lower than workable range | Delta FW algorithm |  | 1. Replace service part |  | Auxiliary power
00800B | 5 volt for CAN bus is lower than workable range | Delta FW algorithm |  | 1. Replace service part |  | Auxiliary power
00800C | 12 volt for other system modules is lower than workable range | Delta FW algorithm |  | 1. Replace service part |  | Auxiliary power
00800D | 12 volt for EV communication is lower than workable range | Delta FW algorithm |  | 1. Replace service part |  | Auxiliary power
00800E | 24 volt for relay control is lower than workable range | Delta FW algorithm |  | 1. Replace service part |  | Auxiliary power
008010 | The output current of 5 volt for system controller is higher than workable range | Delta FW algorithm |  | 1. Replace service part |  | Auxiliary power
008011 | The output current of 5 volt for other system modules is higher than workable range | Delta FW algorithm |  | 1. Replace service part |  | Auxiliary power
008012 | The output current of 5 volt for CAN bus is higher than workable range | Delta FW algorithm |  | 1. Replace service part |  | Auxiliary power
008013 | The output current of 12 volt for other system modules is higher than workable range | Delta FW algorithm |  | 1. Replace service part |  | Auxiliary power
008014 | The output current of 12 volt for EV communication is higher than workable range | Delta FW algorithm |  | 1. Replace service part |  | Auxiliary power
008015 | The output current of 24 volt for relay control is higher than workable range | Delta FW algorithm |  | 1. Replace service part |  | Auxiliary power
008016 | The temperature of 12 volt for EV communication is higher than workable range | 1.Receive from Aux power 2. heatsink temperature ≧100±5℃ |  | 1. Replace service part |  | Auxiliary power
008017 | The temperature of 5 volt for other system modules is higher than workable range | 1.Receive from Aux power 2. heatsink temperature ≧ 100±5℃ |  | 1. Replace service part |  | Auxiliary power
008018 | The temperature of 24 volt for relay control is higher than workable range | 1.Receive from Aux power 2. heatsink temperature ≧ 100±5℃ |  | 1. Replace service part |  | Auxiliary power
008019 | The ambinet temperature of auxiliary power is higher than workable range | 1.Receive from Aux power 2. ≧90±5℃ for 2 second |  | 1. Replace service part |  | Auxiliary power
009001 | GFD trigger | 1.Receive from Relay control (R < 100ohm/V) |  | 1. Replaec charging gun and charging cable if damaged 2. If charging gun and charging cable are well function, replace relay control board. |  | CCS Charging plug or CHAdeMO plug Relay control board
009003 | GFD pre-warnning | 1.Receive from Relay control (100ohm/V < R < 150ohm/V) |  | 1. Replaec charging gun and charging cable if damaged 2. If charging gun and charging cable are well function, replace relay control board. |  | CCS Charging plug or CHAdeMO plug Relay control board
009004 | GFD self-test fail | 1.Receive from Relay control (Self-test-R >70kohm or Self-test-R <30kohm) |  | 1. Replaec charging gun and charging cable if damaged 2. If charging gun and charging cable are well function, replace relay control board. |  | CCS Charging plug or CHAdeMO plug Relay control board
00A001 | Input contactor 1 is welding | 1.CSU can communication with SMR at the end of charging |  | 1. Replace service part |  | AC Contactor
00A002 | Input contactor 1 is drived fault | 1.CSU can't communication with SMR at the begin of charging |  | 1. Replace service part |  | AC Contactor
00A003 | Input contactor 2 is welding | 1.CSU can communication with SMR at the end of charging |  | 1. Replace service part |  | AC Contactor
00A004 | Input contactor 2 is drived fault | 1.CSU can't communication with SMR at the begin of charging |  | 1. Replace service part |  | AC Contactor
00A005 | The positive side of output relay for CCS charging is welding | FW not support |  | N/A |  | N/A
00A006 | The positive side of output relay for CCS charging is drived fault
00A007 | The positive side of output relay for CHAdeMO charging is welding
00A008 | The positive side of output relay for CHAdeMO charging is drived fault
00A009 | The negative side of output relay for CCS charging is welding
00A00A | The negative side of output relay for CCS charging is drived fault
00A00B | The negative side of output relay for CHAdeMO charging is welding
00A00C | The negative side of output relay for CHAdeMO charging is drived fault
00B001 | The firmware update of auxiliary power module is failure | Auxiliary power FW can not updated by CSU BA. |  | 1. If LCM shows 005008, replace CHAdeMO CSU, then try again 2. If LCM does not display 005008, replace auxiliary power module |  | CHAdeMO CSU Auxiliary power
00B002 | The firmware update of relay control module is failure | Relay control module FW can not updated by CSU BA. |  | 1. If LCM shows 005009, replace CHAdeMO CSU, then try again 2. If LCM does not display 005009, replace relay control module |  | CHAdeMO CSU Relay control module
00B003 | The firmware update of LCM module is failure | LCM module FW can not updated by CSU BA. |  | 1. Replace service part |  | LCM module
00B004 | The firmware update of CCS charging module is failure | CSU CA FW can not updated by CSU BA. |  | 1. Replace service part |  | CCS CSU
00B005 | The firmware update of CHAdeMO charging module is failure | CSU BA FW can not updated by USB. |  | 1. Replace service part |  | CCS CSU
00B006 | The firmware update of power converter module is failure | SMR FW can not updated by CSU BA. |  | 1. If LCM shows 005006, replace CHAdeMO CSU, then try again 2. If LCM does not display 005009, replace SMR |  | CHAdeMO CSU SMR
00C001 | PLC module for CCS charging is broken | PLC module of CSU CA broken. |  | 1. Replace service part |  | CCS CSU
00C002 | CCS1 proximity is disconnected | Delta FW algorithm |  | 1. Check CCS1 proximity signal from charging gun to inside of DC wallbox 2. If the signal wire is damaged, replace charging gun 3. If the signal wire is ok, replace CCS CSU |  | CCS charging plug CCS CSU
00C003 | stop charging by CCS EV | 1.During charging, pilot status from C to B |  | Stop by EV. Check setting or information on EV |  | N/A
00D001 | No charging permission come from CHAdeMO EV | Delta FW algorithm |  | 1. Check CHAdeMO permission signal from charging gun to inside of DC wallbox 2. If the signal wire is damaged, replace charging gun 3. If the signal wire is ok, replace CHAdeMO CSU |  | CHAdeMO charging plug CHAdeMO CSU
00D002 | Battery malfunction come from CHAdeMO EV | 1.Charger doesn't detect battery voltage after isolation test. | V | 1. Check EV's model name and contact EV's maker 2. Download log file and contact BU Service |  | N/A
00D003 | Battery incompatibility with CHAdeMO EV | 1.Receive H'102[4] = 1 from EV | V | 1. Check EV's model name and contact EV's maker 2. Download log file and contact BU Service |  | N/A
00D006 | Present output current is different from target current | 1.Receive H'102.4.2 = 1 from EV | V | 1. Check other EV with the same DC wallbox 2. Replace service part if problem exist 3. Download log file and contact BU Service |  | SMR module
00D007 | Battery OTP come from CHAdeMO EV | 1.Receive H'102.4.3 = 1 from EV |  | 1. EV's battery temperature too high, please cool down then try again. |  | N/A
00D008 | Present output voltage is different from target voltage | 1.Receive H'102.4.4 = 1 from EV | V | 1. Check other EV with the same DC wallbox 2. Replace service part if problem exist 3. Download log file and contact BU Service |  | SMR module
00D009 | Position shift alarm is come from CHAdeMO EV | 1.Receive H'102.5.1 = 1 from EV |  | 1. Change position shift back to location "P", then try again. |  | N/A
00D00A | EV other fault is come from CHAdeMO EV | 1.Receive H'102.5.2 = 1 from EV |  | 1. Check EV's model name and contact EV's maker |  | N/A
00D00B | CHAdeMO connector lock is broken | Delta FW algorithm |  | 1. Check the lock on the CHAdeMO charging gun, then try again. 2. If this problem still exist, replace charging gun |  | CHAdeMO charging plug
00D00C | CHAdeMO proximity disconnection | Delta FW algorithm |  | 1. Check CHAdeMO permission signal from charging gun to inside of DC wallbox 2. If the signal wire is damaged, replace charging gun 3. If the signal wire is ok, replace CHAdeMO CSU |  | CHAdeMO charging plug CHAdeMO CSU